## Activity-Checklist_25.02.26
AGEL CIVIL and ELECTRICAL Package > Sub-Package > Activity > Sub-Activity Structure along with Inspection Checklist Mapping
| As defined in PULSE+DRS Platform Master Data |  |  |  | To be selected by Contractor during creation of RFI | As per the SAP PO UoM
Sr. No. | Package | Sub-Package | Activity | Sub-Activity | Min. Unit of RFI (Per Table / Per Inverter / Per Block) | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checkpoint Code | Inspection Checkpoint Name | Inspection Checkpoint Description | Inspection Checklist Name | Preceding Inspection Checkpoint to be completed before raising RFI | Activity Dependency |  |  |  | Remarks
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - MMS | Per Table | EA | A.1.1.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | - | -
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - MMS | Per Table | EA | A.1.1.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | A.1.1.1
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - MMS | Per Table | EA | A.1.1.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | A.1.1.2
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - MMS | Per Table | EA | A.1.1.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | A.1.1.3
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - Inverter | Per Inverter | EA | A1.2.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | - | -
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - Inverter | Per Inverter | EA | A1.2.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | A1.2.1
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - Inverter | Per Inverter | EA | A1.2.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | A1.2.2
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - Inverter | Per Inverter | EA | A1.2.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | A1.2.3
A.1.3 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - LT Cable Hanger System | Per Inverter | EA | A1.3.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | - | -
A.1.3 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - LT Cable Hanger System | Per Inverter | EA | A1.3.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | A1.3.1
A.1.3 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - LT Cable Hanger System | Per Inverter | EA | A1.3.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | A1.3.2
A.1.3 | Civil | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) | Piling - LT Cable Hanger System | Per Inverter | EA | A1.3.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | A1.3.3
B.1.1 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | - | -
B.1.1 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | B1.1.1
B.1.1 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.3 | Pre Pour Inspection for Column & Slab - Cast-in-Situ | Fixing of reinforcements (as per BBS), positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Cordinates & Location of opening, cut-outs (Size as per drawing) upto concreting works (mixing & pouring). | C_1_Pour Card | B1.1.2
B.1.1 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.4 | Post Pour Inspection for Column & Slab - Cast-in-Situ | Physical Dimension of structure as per drawing & appearnce (free of defect, deformations, etc.,.) and curing etc. | C_8_Post Pour Check | B1.1.3
B.1.1 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.5 | Canopy Erection with Sheeting after Grouting | Fixing of nut & bolts in erected structure prior to final allignment check and tightening | C_11_Dimensional Assembly,Fitup Check Report and Inspection of Structural Alignment | B1.1.4
B.1.1 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.6 | Grouting | Readiness of grouting area (hacking, cleaning, soaking, shuttering,mixing,cube sampling works), grout pouring and acceptance of grout cube strength test results | C_34_Grouting Works | B1.1.5
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | - | -
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.2 | Gravel Filling | Filling of suitable size gravels / sand as per drawing (Approved source material, physically Tested as per SFQP & accepted by Quality) | C_27_Gravel Filling Works | B1.2.1
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.3 | Sand Relative Density Test | To check the relative density of sand | C_15_FDD Test by Sand Replacement Method | B1.2.2
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.4 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying & finishing upto required level | C_36_PCC Works | B1.2.3
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.5 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and upto concreting works | C_1_Pour Card | B1.2.4
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.6 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | B1.2.5
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.7 | Pre Pour Inspection for 1st Lift Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | B1.2.6
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.8 | Post Pour Inspection for 1st Lift Wall | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | B1.2.7
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.9 | Backfiling Layer Wise | Layer-wise filling, compaction & testing in each layer untill achieving accepted test result. | C_16_FDD Test by Core Cutter Method | B1.2.8
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.10 | Pre Pour Inspection for 2nd Lift Wall with Rail | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | B1.2.9
B.1.2 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.11 | Post Pour Inspection for 2nd Lift Wall with Rail | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | B1.2.10
B.1.3 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | -
B.1.3 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | B1.3.1
B.1.3 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | B1.3.2
B.1.4 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | B1.4.1 | Sub Grade Compaction Test & Leveling | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | - | -
B.1.4 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | B1.4.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level | C_36_PCC Works | B1.4.1
B.1.4 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | B1.4.3 | Pre Pour Inspection for RCC Block | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and concreting works | C_1_Pour Card | B1.4.2
B.1.4 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | B1.4.4 | Post Pour Inspection for RCC Block | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | B1.4.3
B.1.5 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | B1.5.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | - | -
B.1.5 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | B1.5.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | B1.5.1
B.1.5 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | B1.5.3 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | B1.5.2
B.1.5 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | B1.5.4 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | B1.5.3
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.1 | Levelling & Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | - | -
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.2 | Rubble Soling Test | Laying of requisite size rubble soling material upto compaction | C_27_Gravel Filling Works | B1.6.1
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.3 | Pre-Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | B1.6.2
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.4 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | B1.6.3
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.5 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) with rectifications if any. And appllication of protecting coating paint | C_8_Post Pour Check | B1.6.4
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.6 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | B1.6.5
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.7 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | B1.6.6
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.8 | Pre Pour Inspection for Slab | Fixing & tighntness of shuttering supports, leak-proof arranegments, Reinforcement fixing, positioning of pockets/inserts/embedments. And upto concreting works | C_1_Pour Card | B1.6.7
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.9 | Post Pour Inspection for Slab | Surface level/slope & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectification of defects if any | C_8_Post Pour Check | B1.6.8
B.1.6 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | B1.6.10 | Leak Test, Rectification of Defects, Acceptance of Corrective Actions Taken (if applicable) | Leak Test | C_8_Post Pour Check | B1.6.9
B.1.7 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | B1.7.1 | Sub Grade Compaction Test (including Rubble Soiling) | Levelling & compaction test of base & Laying of rubble | C_16_FDD Test by Core Cutter Method | - | -
B.1.7 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | B1.7.2 | Pre Pour Inspection for Sump PCC | Level & Grid Marking for PCC Laying & finishing upto required level and concreting works | C_36_PCC Works | B1.7.1
B.1.7 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | B1.7.3 | Pre Pour Inspection for Sump Raft | Fixing of reinforcements as per drawing prior to shutter board fixing, positioning of inserts & embedments (if any) and concreting works | C_1_Pour Card | B1.7.2
B.1.7 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | B1.7.4 | Post Pour Inspection for Sump Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | B1.7.3
B.1.7 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | B1.7.5 | Pre Pour Inspection for Dyke Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | B1.7.4
B.1.7 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | B1.7.6 | Post Pour Inspection for Dyke Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | B1.7.5
B.1.8 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Fencing | Block | Not Applicable | B1.8.1 | Fencing Pole Concrete Works Check | Markig of locations of posts, hole depth, Alignment, Verticality & level of Fence Post & concreting works as per drawing | C_47 USS,IDT,PSS Fencing Concrete Pole Works | - |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.1
B.1.8 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Fencing | Block | Not Applicable | B1.8.2 | Fixing of Fencing Wire, Concertina, Gates as per drawing with Painting | Fixing of Fencing wire, concertina, Gates as per drawing with painting | C_10_Installation & Erection of Honey Comb Fence Post & Accessories | B1.8.1
B.1.9 | Civil | IDT Civil & Structural | IDT Civil & Structural | IDT Gravel Laying | Block | Not Applicable | B1.9.1 | Gravel Filling | Inspection of Gravel Filling Works | C_27_Gravel Filling Works | - |  |  |  | C.3.1, D.1.6, D.2.1, D.2.3, D.3.1
C.1.1 | Civil | MMS Installation | MMS Installation | MMS Installation | Per Table | MT | C1.1.1 | MMS Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_1 MMS Installation Protocol- Fixed Tilt 2) C_29_1 MMS Installation Protocol - Tracker | A.1.1.3 |  | A.1.1
D.1.1 | Civil | Module & Robot Structure installation | Module & Robot Structure installation | Module Installation | Per Table | EA | D1.1.1 | Module Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts) | 1) C_28_2 Module Installation Protocol- Fixed Tilt 2) C_29_2 Module Installation Protocol - Tracker | C1.1.1 |  |  | B.1.1
D.1.2 | Civil | Module & Robot Structure installation | Module & Robot Structure installation | Installation of binders/clips, bridges | Per Table | Not Applicable | D1.2.1 | Final Inspection of Alignment, Torquing of Flexible Bridges, Clips and Binders | ? | ? | D1.1.1 |  |  |  | C.1.1,A1.3,B1.1
E.1.1 |  |  | 0 | Piling - Robotic Docking System |  |  | E1.1.1 |  | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori.
E.1.1 |  |  | 0 | Piling - Robotic Docking System |  |  | E1.1.2 |  | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. |  | E1.1.1
E.1.1 |  |  | 0 | Piling - Robotic Docking System |  |  | E1.1.3 |  | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP |  | E1.1.2
E.1.1 |  |  | 0 | Piling - Robotic Docking System |  |  | E1.1.4 |  | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | E1.1.3
E.1.2 | Civil | Robot Works | Robot Works | Installation of docking & reverse stations | Per Table | Not Applicable | E1.2.1 | Final Inspection of Alignment, Torquing of Docking and Return Stations | ? | ? | E1.1.4 |  |  |  | C.1.1,A1.3,B1.1
F.1.1 |  |  | Equipment Installation & Testing and Cable Termination |  |  |  | F1.1.1 | IDT and Accessories Installation | IDT Installation along with Accessories | A1_IDT and Accessories Installation
F.1.1 |  |  | Equipment Installation & Testing and Cable Termination |  |  |  | F1.1.2 | IDT Electrical & Oil Filtration Testing | Electrical and Oil Filtration testing of IDT after installation | A2_IDT Oil Filled Transformer Oil Filtration and Testing + Upload of 3 testing reports | F1.1.1
F.1.1 |  |  | Equipment Installation & Testing and Cable Termination |  |  |  | F1.1.3 |  | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | A3_IDT Oil Filled Transformer HT, LT and Control Cable Termination, Equipment Earthing | F1.1.2
F.1.2 |  |  | Equipment Installation & Testing and Cable Termination |  |  |  | F1.2.1 |  | Panel installation and Panel testing | C1_HT Panel Installation & Testing + Upload of Testing Report
F.1.2 | Electrical | AC / LT Network | Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | F1.2.2 | HT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, HT cable end termination, Torquing, Equipment body Earthing | C2_Cable Termination & Equipment Body Earthing | F1.2.1
F.1.3 | Electrical | AC / LT Network | Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | F1.3.1 | LT Panel Installation & Testing | Panel installation and Panel testing | B1_LT Panel Installation & Testing + Upload of Testing Report | - |  | A.2.1
F.1.3 | Electrical | AC / LT Network | Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | F1.3.2 | LT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | B2_Cable Termination & Equipment Body Earthing | F1.3.1
F.1.4 | Electrical | AC / LT Network | Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | F1.4.1 | Auxiliary Transformer Installation & Testing | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | D1_Auxiliary Transformer Installation & Testing + Upload of Testing Report | - |  | A.2.3
F.1.4 | Electrical | AC / LT Network | Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | F1.4.2 | Auxiliary Transformer Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | D2_Cable Termination & Equipment Body Earthing | F1.4.1
F.1.5 | Electrical | AC / LT Network | Equipment Installation & Testing and Cable Termination | NIFPS | Block | LOT | F1.5.1 | NIFPS Installation & Testing | NIFPS Installation & Testing | No Checklist; only testing report to be uploaded | - |  | A.2.4
F.2.1 | Electrical | AC / LT Network | Laying of Cable and Cable Management System | LT Cable Laying - Inverter to LT Panel | Per Inverter | M | F2.1.1 | Cable Drum IR Test and Cable Hanging for Above-Ground Section | Cable drum IR test and Cable hanging for above-ground section | F1_1 Cable Drum IR test, Cable Hanging | - |  |  | D.2.5
F.2.2 | Electrical | AC / LT Network | Laying of Cable and Cable Management System | LT Cable Mgmt System Laying | Block | Not Applicable | F2.2.1 | Messenger Wire Hanging | Messenger wire hanging | F1_2 Messenger Wire Hanging | - | - | -
F.3.1 | Electrical | AC / LT Network | Earthing | Grid Earthing | Block | M | F3.1.1 | Grid Earthing Work & Testing | Grid Earthing work & Testing | H4_Grid Earthing | F1.1.3; F1.2.2; F1.3.2; F1.4.2; F1.5.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.1.6
G.1.1 | Electrical | DC Network | Equipment Installation & Testing and Cable Termination | String Inverter | Per Inverter | NO | G1.1.1 | Inverter Installation, Testing & Equipment Earthing | Inverter installation; Equipment body Earthing | H3_String Inverter Installation & Earthing | - |  | A.1.2
G.1.2 | Electrical | DC Network | Equipment Installation & Testing and Cable Termination | String Inverter - LT Cable Termination | Per Inverter | NO | G1.2.1 | LT Cable Termination at Inverter | LT Cable Lugging, Crimping, Sleeving & Torquing | F3_ LT Cable Termination | F2.1.1; G1.1.1
G.1.3 | Electrical | DC Network | Equipment Installation & Testing and Cable Termination | String Inverter - String Formation | Per Inverter | NO | G1.3.1 | MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | H2_MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | -
G.2.1 | Electrical | DC Network | Laying of Cable and Cable Management System | DC Cable Works | Per Inverter | M | G2.1.1 | Trench Excavation, DC Cable Laying, Dressing, Conduiting and PU Foam Sealing | Trench excavation, DC cable laying, dressing, conduiting (Modules to Inverter) | H1_Trench Excavation, DC Cable Laying and Conduiting | - |  |  |  | C.1.1
G.3.1 | Electrical | DC Network | Earthing | Earthing of tables | Per Table | M | G3.1.1 | Table-to-Table & Grid Earthing Work Testing | Table-to-table & grid earthing work testing | H4_Grid Earthing | - |  |  | B.1.1
G.4.1 | Electrical | HT Cabling | HT Cable Laying & Termination | HT cable - Pre-Laying | Block | KM | G.4.1.1 | HT cable - Pre-Laying | i. Check the IR of the cable drum ii. Excavation of Trench iii. First layer of Sand Bedding | 16-HT Cable Field Quality Protocol (Pre-Laying Section) | -
G.4.2 | Electrical | HT Cabling | HT Cable Laying & Termination | HT Cable - Laying and Termination | Block | KM | G.4.1.2 | HT Cable - Laying and Termination | i. Cable laying with proper routine ii. Bricks laying properly iii. Second layer sand bedding iv. Backfilling of trench also with FO cable and Caution Tap v. Check the cable straight through and End Termination Joints. | 16-HT Cable Field Quality Protocol (Laying Section) | G.4.1.1 |  |  |  | C.1.1
G.4.3 | Electrical | HT Cabling | HT Cable Laying & Termination | HT Cable - Testing | Block | KM | G.4.1.3 | HT Cable - Testing | i. VLF of the whole line Ii. Megger of Line | 16-HT Cable Field Quality Protocol (Pre-Commissioning Section) | G.4.1.2 |  |  | B.1.1
Note on E5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on M5: Hemdeep Padalia: This will be used to sequence inspection checkpoints (within a sub-activity) and order of sub-activity in which RFI can be created
Note on J25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on M32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this
Note on M33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this - to be checked if both lift walls can be done in parallel
Note on M75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on M77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on M79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on M81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on L85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on M85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In addition to mentioned checkpoints, need to ask Kamalesh if there is any other pre-requisite Reply: Ok
Note on L86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on M87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Also include LT Cable Laying here - D2.1.1 Reply: Done Reply: Done
Note on L90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained

## Activity-Checklist_06.05.2026
AGEL CIVIL and ELECTRICAL Package > Sub-Package > Activity > Sub-Activity Structure along with Inspection Checklist Mapping
|  | As defined in PULSE+DRS Platform Master Data | [7 empty] | To be selected by Contractor during creation of RFI | As per the SAP PO UoM
Change Task | Sr. No. | Package | EPC Service code (BBU as of May'26) | Sub-Package (New) | Sub-Package (Old) | Activity (New) | Activity (Old) | Sub-Activity (New) | Sub-Activity (Old) | Min. Unit of RFI (Per Table / Per Inverter / Per Block) | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checkpoint Code | Inspection Checkpoint Name (New) | Inspection Checkpoint Name (Old) | Inspection Checkpoint Description (Updated) | Inspection Checklist Name (Updated) | Preceding Inspection Checkpoint (Updated) | Activity Dependency |  |  |  | Remarks
Sub-Package Name Change | A.1.1 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.1 | Pre Pour Inspection - Pile | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | - | -
Sub-Package Name Change | A.1.1 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.2 | Pre Pour Inspection - Pile Cap | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | A.1.1.1
Sub-Package Name Change | A.1.1 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.3 | Post Pour Inspection | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | A.1.1.2
New Checkpoint | A.1.1 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | New | Piling - MMS | New | Piling - MMS | New | Per Table | EA | A.1.1.4 | Epoxy Coating | New | Application of epoxy coat as per SOP | 87_Bitumen & Epoxy Paint Checklists | -
Sub-Package Name Change | A.1.1 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.5 | Routine Testing | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | A.1.1.3
Sub-Package Name Change | A.1.2 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.1 | Pre Pour Inspection - Pile | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | - | -
Sub-Package Name Change | A.1.2 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.2 | Pre Pour Inspection - Pile Cap | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | A1.2.1
Sub-Package Name Change | A.1.2 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.3 | Post Pour Inspection | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | A1.2.2
New Checkpoint | A.1.1 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | New | Piling - Inverter | New | Piling - Inverter | New | Per Inverter | EA | A.1.2.4 | Epoxy Coating | New | Application of epoxy coat as per SOP | 87_Bitumen & Epoxy Paint Checklists | -
Sub-Package Name Change | A.1.2 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.5 | Routine Testing | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | A1.2.3
Sub-Package Name Change | A.1.3 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.3.1 | Pre Pour Inspection - Pile | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | - | -
Sub-Package Name Change | A.1.3 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.3.2 | Pre Pour Inspection - Pile Cap | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | A1.3.1
Sub-Package Name Change | A.1.3 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.3.3 | Post Pour Inspection | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | A1.3.2
New Checkpoint | A.1.1 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | New | Piling - LT Cable Hanger System | New | Piling - LT Cable Hanger System | New | Per Inverter | EA | A.1.3.4 | Epoxy Coating | New | Application of epoxy coat as per SOP | 87_Bitumen & Epoxy Paint Checklists | -
Sub-Package Name Change | A.1.3 | Civil | 120021756 | Piling (MMS, Inverter, LT Cable Hangers) | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.3.5 | Routine Testing | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | A1.3.3
Sub-Package + Activity + Inspection Checkpoint + Additional Checklist | B.1.1 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.1 | Inspection - Up to NGL - Stage 1 | Pre Pour Inspection - Pile | If Open Foundation: Inspection of Gravel, GSB, Rubble, Sand filling, PCC, Footings / raft, and Columns -Filling of suitable size gravels / sand as per drawing (approved source material, physically tested as per SFQP & accepted by Quality) and compacted thickness -Level & Grid Marking for PCC Laying & finishing upto required level -Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, shuttering tightness, verticality, alignment checking prior to concreting works If Micropiling Foundation: Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | If Open Foundation: C_27_Gravel Filling Works + C_36_PCC Works + C_1_Pour Card If Micropiling Foundation: C_14_1 Micro Pile Checklist | - | -
Sub-Package + Activity + Inspection Checkpoint + Additional Checklist | B.1.1 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.2 | Inspection - Up to NGL - stage 2 | Pre Pour Inspection - Pile Cap | If Open Foundation: Inspection of Footings/ Raft/ Columns up to NGL + Backfilling layer wise: -Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.) -Layer-wise filling, compaction & testing in each layer untill achieving accepted test result If Micropiling Foundation: Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | If Open Foundation: C_8_Post Pour Check + C_16_FDD Test by Core Cutter Method If Micropiling Foundation: C_14_2 Micro Pile Cap Checklist | B1.1.1
Sub-Package + Activity changes | B.1.1 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.3 | Pre Pour Inspection for Column & Slab - Cast-in-Situ | Pre Pour Inspection for Column & Slab - Cast-in-Situ | Fixing of reinforcements (as per BBS), positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Cordinates & Location of opening, cut-outs (Size as per drawing) upto concreting works (mixing & pouring). | C_1_Pour Card | B1.1.2
Sub-Package + Activity changes | B.1.1 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.4 | Post Pour Inspection for Column & Slab - Cast-in-Situ | Post Pour Inspection for Column & Slab - Cast-in-Situ | Physical Dimension of structure as per drawing & appearnce (free of defect, deformations, etc.,.) and curing etc. | C_8_Post Pour Check | B1.1.3
Sub-Package + Activity changes | B.1.1 | Civil | 120036458 | IDT Civil & Structural - 2 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.5 | Canopy Erection with Sheeting after Grouting | Canopy Erection with Sheeting after Grouting | Fixing of nut & bolts in erected structure prior to final allignment check and tightening | C_11_Dimensional Assembly,Fitup Check Report and Inspection of Structural Alignment | B1.1.4
Sub-Package + Activity changes | B.1.1 | Civil | 120036458 | IDT Civil & Structural - 2 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil & Structural | IDT Civil - HT / LT Platform | IDT Civil - HT / LT Platform | Block | Not Applicable | B1.1.6 | Grouting | Grouting | Readiness of grouting area (hacking, cleaning, soaking, shuttering,mixing,cube sampling works), grout pouring and acceptance of grout cube strength test results | C_34_Grouting Works | B1.1.5
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.1 | Sub Grade Compaction Test | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | - | -
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.2 | Gravel Filling | Gravel Filling | Filling of suitable size gravels / sand as per drawing (Approved source material, physically Tested as per SFQP & accepted by Quality) | C_27_Gravel Filling Works | B1.2.1
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.3 | Sand Relative Density Test | Sand Relative Density Test | To check the relative density of sand | C_15_FDD Test by Sand Replacement Method | B1.2.2
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.4 | Pre Pour Inspection for PCC | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying & finishing upto required level | C_36_PCC Works | B1.2.3
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.5 | Pre Pour Inspection for Raft | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and upto concreting works | C_1_Pour Card | B1.2.4
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.6 | Post Pour Inspection for Raft | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | B1.2.5
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.7 | Pre Pour Inspection for 1st Lift Wall | Pre Pour Inspection for 1st Lift Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | B1.2.6
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.8 | Post Pour Inspection for 1st Lift Wall | Post Pour Inspection for 1st Lift Wall | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | B1.2.7
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.9 | Backfiling Layer Wise | Backfiling Layer Wise | Layer-wise filling, compaction & testing in each layer untill achieving accepted test result. | C_16_FDD Test by Core Cutter Method | B1.2.8
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.10 | Pre Pour Inspection for 2nd Lift Wall with Rail | Pre Pour Inspection for 2nd Lift Wall with Rail | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | B1.2.9
Sub-Package + Activity changes | B.1.2 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil & Structural | IDT Civil - Transformer Platform | IDT Civil - Transformer Platform | Block | Not Applicable | B1.2.11 | Post Pour Inspection for 2nd Lift Wall with Rail | Post Pour Inspection for 2nd Lift Wall with Rail | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | B1.2.10
Sub-Package + Activity changes | B.1.3 | Civil | 120036458 | IDT Civil & Structural - 2 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural - Cable Rack | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.1 | Pre Pour Inspection - Pile | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | -
Sub-Package + Activity changes | B.1.3 | Civil | 120036458 | IDT Civil & Structural - 2 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural - Cable Rack | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.2 | Pre Pour Inspection - Pile Cap | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | B1.3.1
Sub-Package + Activity changes | B.1.3 | Civil | 120036458 | IDT Civil & Structural - 2 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural - Cable Rack | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.3 | Post Pour Inspection | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | B1.3.2
Sub-Package + Activity changes | B.1.4 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Aux Transformer Platform | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | IDT Civil - Aux Transformer Platform | Block | Not Applicable | B1.4.1 | Sub Grade Compaction Test & Leveling | Sub Grade Compaction Test & Leveling | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | - | -
Sub-Package + Activity changes | B.1.4 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Aux Transformer Platform | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | IDT Civil - Aux Transformer Platform | Block | Not Applicable | B1.4.2 | Pre Pour Inspection for PCC | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level | C_36_PCC Works | B1.4.1
Sub-Package + Activity changes | B.1.4 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Aux Transformer Platform | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | IDT Civil - Aux Transformer Platform | Block | Not Applicable | B1.4.3 | Pre Pour Inspection for RCC Block | Pre Pour Inspection for RCC Block | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and concreting works | C_1_Pour Card | B1.4.2
Sub-Package + Activity changes | B.1.4 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Aux Transformer Platform | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | IDT Civil - Aux Transformer Platform | Block | Not Applicable | B1.4.4 | Post Pour Inspection for RCC Block | Post Pour Inspection for RCC Block | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | B1.4.3
Sub-Package + Activity changes | B.1.5 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - NIFPS Foundation | IDT Civil & Structural | IDT Civil - NIFPS Foundation | IDT Civil - NIFPS Foundation | Block | Not Applicable | B1.5.1 | Sub Grade Compaction Test | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | - | -
Sub-Package + Activity changes | B.1.5 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - NIFPS Foundation | IDT Civil & Structural | IDT Civil - NIFPS Foundation | IDT Civil - NIFPS Foundation | Block | Not Applicable | B1.5.2 | Pre Pour Inspection for PCC | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | B1.5.1
Sub-Package + Activity changes | B.1.5 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - NIFPS Foundation | IDT Civil & Structural | IDT Civil - NIFPS Foundation | IDT Civil - NIFPS Foundation | Block | Not Applicable | B1.5.3 | Pre Pour Inspection for Wall | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | B1.5.2
Sub-Package + Activity changes | B.1.5 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - NIFPS Foundation | IDT Civil & Structural | IDT Civil - NIFPS Foundation | IDT Civil - NIFPS Foundation | Block | Not Applicable | B1.5.4 | Post Pour Inspection for Wall | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | B1.5.3
Sub-Package + Activity changes | B.1.6 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.1 | Levelling & Compaction Test | Levelling & Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | - | -
Sub-Package + Activity changes | B.1.6 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.2 | Rubble Soling Test | Rubble Soling Test | Laying of requisite size rubble soling material upto compaction | C_27_Gravel Filling Works | B1.6.1
Sub-Package + Activity changes | B.1.6 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.3 | Pre-Pour Inspection for PCC | Pre-Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | B1.6.2
Sub-Package + Activity changes | B.1.6 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.4 | Pre Pour Inspection for Raft | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | B1.6.3
Sub-Package + Activity changes | B.1.6 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.5 | Post Pour Inspection for Raft | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) with rectifications if any. And appllication of protecting coating paint | C_8_Post Pour Check | B1.6.4
Sub-Package + Activity changes | B.1.6 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.6 | Pre Pour Inspection for Wall | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | B1.6.5
Sub-Package + Activity changes | B.1.6 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.7 | Post Pour Inspection for Wall | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | B1.6.6
Sub-Package + Activity changes | B.1.6 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.8 | Pre Pour Inspection for Slab | Pre Pour Inspection for Slab | Fixing & tighntness of shuttering supports, leak-proof arranegments, Reinforcement fixing, positioning of pockets/inserts/embedments. And upto concreting works | C_1_Pour Card | B1.6.7
Sub-Package + Activity changes | B.1.6 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.9 | Post Pour Inspection for Slab | Post Pour Inspection for Slab | Surface level/slope & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectification of defects if any | C_8_Post Pour Check | B1.6.8
Sub-Package + Activity changes | B.1.6 | Civil | 120036458 | IDT Civil & Structural - 2 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - BOP | IDT Civil & Structural | IDT Civil - BOP | IDT Civil - BOP | Block | Not Applicable | B1.6.10 | Leak Test, Rectification of Defects, Acceptance of Corrective Actions Taken (if applicable) | Leak Test, Rectification of Defects, Acceptance of Corrective Actions Taken (if applicable) | Leak Test | C_8_Post Pour Check | B1.6.9
Sub-Package + Activity changes | B.1.7 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Sump | IDT Civil & Structural | IDT Civil - Sump | IDT Civil - Sump | Block | Not Applicable | B1.7.1 | Sub Grade Compaction Test (including Rubble Soiling) | Sub Grade Compaction Test (including Rubble Soiling) | Levelling & compaction test of base & Laying of rubble | C_16_FDD Test by Core Cutter Method | - | -
Sub-Package + Activity changes | B.1.7 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Sump | IDT Civil & Structural | IDT Civil - Sump | IDT Civil - Sump | Block | Not Applicable | B1.7.2 | Pre Pour Inspection for Sump PCC | Pre Pour Inspection for Sump PCC | Level & Grid Marking for PCC Laying & finishing upto required level and concreting works | C_36_PCC Works | B1.7.1
Sub-Package + Activity changes | B.1.7 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Sump | IDT Civil & Structural | IDT Civil - Sump | IDT Civil - Sump | Block | Not Applicable | B1.7.3 | Pre Pour Inspection for Sump Raft | Pre Pour Inspection for Sump Raft | Fixing of reinforcements as per drawing prior to shutter board fixing, positioning of inserts & embedments (if any) and concreting works | C_1_Pour Card | B1.7.2
Sub-Package + Activity changes | B.1.7 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Sump | IDT Civil & Structural | IDT Civil - Sump | IDT Civil - Sump | Block | Not Applicable | B1.7.4 | Post Pour Inspection for Sump Raft | Post Pour Inspection for Sump Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | B1.7.3
Sub-Package + Activity changes | B.1.7 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Sump | IDT Civil & Structural | IDT Civil - Sump | IDT Civil - Sump | Block | Not Applicable | B1.7.5 | Pre Pour Inspection for Dyke Wall | Pre Pour Inspection for Dyke Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | B1.7.4
Sub-Package + Activity changes | B.1.7 | Civil | 120021282 | IDT Civil & Structural - 1 | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil - Sump | IDT Civil & Structural | IDT Civil - Sump | IDT Civil - Sump | Block | Not Applicable | B1.7.6 | Post Pour Inspection for Dyke Wall | Post Pour Inspection for Dyke Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | B1.7.5
Sub-Package + Activity changes | B.1.8 | Civil | 120036458 | IDT Civil & Structural - 2 | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing | IDT Fencing & Gravel Laying | IDT Fencing | IDT Fencing | Block | Not Applicable | B1.8.1 | Fencing Pole Concrete Works Check | Fencing Pole Concrete Works Check | Markig of locations of posts, hole depth, Alignment, Verticality & level of Fence Post & concreting works as per drawing | C_47 USS,IDT,PSS Fencing Concrete Pole Works | - |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.1
Sub-Package + Activity changes | B.1.8 | Civil | 120036458 | IDT Civil & Structural - 2 | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing | IDT Fencing & Gravel Laying | IDT Fencing | IDT Fencing | Block | Not Applicable | B1.8.2 | Fixing of Fencing Wire, Concertina, Gates as per drawing with Painting | Fixing of Fencing Wire, Concertina, Gates as per drawing with Painting | Fixing of Fencing wire, concertina, Gates as per drawing with painting | C_10_Installation & Erection of Honey Comb Fence Post & Accessories | B1.8.1
Sub-Package + Activity changes | B.1.9 | Civil | 120036458 | IDT Civil & Structural - 2 | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Gravel Laying | IDT Fencing & Gravel Laying | IDT Gravel Laying | IDT Gravel Laying | Block | Not Applicable | B1.9.1 | Gravel Filling | Gravel Filling | Inspection of Gravel Filling Works | C_27_Gravel Filling Works | - |  |  |  | C.3.1, D.1.6, D.2.1, D.2.3, D.3.1
No Change | C.1.1 | Civil | 120036447 | MMS Installation | MMS Installation | MMS Installation | MMS Installation | MMS Installation | MMS Installation | Per Table | MT | C1.1.1 | MMS Installation and Assembly | MMS Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_1 MMS Installation Protocol- Fixed Tilt 2) C_29_1 MMS Installation Protocol - Tracker | A.1.1.3 |  | A.1.1
Sub-Package Name Change | D.1.1 | Civil | 120036456 | Module, Binders & Bridges Installation | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Module Installation | Module Installation | Module Installation | Module Installation | Per Table | EA | D1.1.1 | Module Installation and Assembly | Module Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts) | 1) C_28_2 Module Installation Protocol- Fixed Tilt 2) C_29_2 Module Installation Protocol - Tracker | C1.1.1 |  |  | B.1.1
New Checkpoint | D.1.2 | Civil | 120036456 | Module, Binders & Bridges Installation | New | Installation of binders / clips, bridges | New | Installation of binders / clips, bridges | New | Per Table | Not Applicable | D1.2.1 | Final Inspection of Alignment, Torquing of Flexible Bridges, Clips and Binders | New | Binders & Bridges checking | Checklist for Binders & Bridges | D1.1.1 |  |  |  | C.1.1,A1.3,B1.1
Sub-Package Name Change | E.1.1 | Civil | 120036457 | Robot Works - Piling, Docking / Reverse Stations Installation | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | Not Applicable | E1.1.1 | Pre Pour Inspection - Pile |  | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist
Sub-Package Name Change | E.1.1 | Civil | 120036457 | Robot Works - Piling, Docking / Reverse Stations Installation | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | Not Applicable | E1.1.2 | Pre Pour Inspection - Pile Cap |  | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | E1.1.1
Sub-Package Name Change | E.1.1 | Civil | 120036457 | Robot Works - Piling, Docking / Reverse Stations Installation | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | Not Applicable | E1.1.3 | Post Pour Inspection |  | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | E1.1.2
New Checkpoint | E.1.1 | Civil | 120036457 | Robot Works - Piling, Docking / Reverse Stations Installation | New | Piling - Robotic Docking System | New | Piling - Robotic Docking System | New | Per Table | Not Applicable | E.1.1.4 | Epoxy Coating | New | Application of epoxy coat as per SOP | 87_Bitumen & Epoxy Paint Checklists | -
Sub-Package Name Change | E.1.1 | Civil | 120036457 | Robot Works - Piling, Docking / Reverse Stations Installation | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | Not Applicable | E1.1.5 | Routine Testing |  | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | E1.1.3
Sub-Package + Activity + Sub-Activity Name changes | E.2.1 | Civil | 120036457 | Robot Works - Piling, Docking / Reverse Stations Installation | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Installation of docking & reverse stations | Robot Structure Installation | Installation of docking & reverse stations | Installation of binders/clips, bridges, docking & reverse stations | Per Table | Not Applicable | E.2.1.1 | Final Inspection of Alignment, Torquing of Docking and Return Stations |  | Inspection Checklist for Installation of Cleaning Robot Structures | 1) Cleaning Robot Installation Checklist_Leapting 2) Cleaning Robot Installation Checklist_Sol Bright 3) Cleaning Robot Installation Checklist_Airtouch | E1.1.3 |  |  |  | C.1.1,A1.3,B1.1
No Change | F.1.1 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | Transformer |  | Per Block | Not Applicable | F1.1.1 | IDT and Accessories Installation |  | IDT Installation along with Accessories | A1_IDT and Accessories Installation | -
No Change | F.1.1 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | Transformer |  | Per Block | Not Applicable | F1.1.2 | IDT Electrical & Oil Filtration Testing |  | Electrical and Oil Filtration testing of IDT after installation | A2_IDT Oil Filled Transformer Oil Filtration and Testing + Upload of 3 testing reports | F1.1.1
No Change | F.1.1 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | Transformer |  | Per Block | Not Applicable | F1.1.3 | Inverter Cable Terminations & Equipment Earthing |  | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | A3_IDT Oil Filled Transformer HT, LT and Control Cable Termination, Equipment Earthing | F1.1.2
No Change | F.1.2 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | HT Panel |  | Per Block | EA | F1.2.1 | HT Panel Installation & Testing |  | Panel installation and Panel testing | C1_HT Panel Installation & Testing + Upload of Testing Report | -
No Change | F.1.2 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | HT Panel |  | Block | EA | F1.2.2 | HT Panel Cable Terminations & Equipment Earthing |  | Cable Lugging, Crimping, Sleeving, HT cable end termination, Torquing, Equipment body Earthing | C2_Cable Termination & Equipment Body Earthing | F1.2.1
No Change | F.1.3 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | LT Panel |  | Block | NO | F1.3.1 | LT Panel Installation & Testing |  | Panel installation and Panel testing | B1_LT Panel Installation & Testing + Upload of Testing Report | - |  | A.2.1
No Change | F.1.3 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | LT Panel |  | Block | NO | F1.3.2 | LT Panel Cable Terminations & Equipment Earthing |  | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | B2_Cable Termination & Equipment Body Earthing | F1.3.1
No Change | F.1.4 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | Auxiliary Transformer |  | Block | SET | F1.4.1 | Auxiliary Transformer Installation & Testing |  | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | D1_Auxiliary Transformer Installation & Testing + Upload of Testing Report | - |  | A.2.3
No Change | F.1.4 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | Auxiliary Transformer |  | Block | SET | F1.4.2 | Auxiliary Transformer Cable Terminations & Equipment Earthing |  | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | D2_Cable Termination & Equipment Body Earthing | F1.4.1
No Change | F.1.5 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Equipment Installation & Testing and Cable Termination |  | NIFPS |  | Block | LOT | F1.5.1 | NIFPS Installation & Testing |  | NIFPS Installation & Testing | No Checklist; only testing report to be uploaded | - |  | A.2.4
No Change | F.2.1 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Laying of Cable and Cable Management System |  | LT Cable Laying - Inverter to LT Panel |  | Per Inverter | M | F2.1.1 | Cable Drum IR Test and Cable Hanging for Above-Ground Section |  | Cable drum IR test and Cable hanging for above-ground section | F1_1 Cable Drum IR test, Cable Hanging | - |  |  | D.2.5
No Change | F.2.2 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Laying of Cable and Cable Management System |  | LT Cable Mgmt System Laying |  | Block | Not Applicable | F2.2.1 | Messenger Wire Hanging |  | Messenger wire hanging | F1_2 Messenger Wire Hanging | - | - | -
No Change | F.3.1 | Electrical | 150014585 | AC / LT Network |  | AC / LT Network - Earthing |  | Grid Earthing |  | Block | M | F3.1.1 | Grid Earthing Work & Testing |  | Grid Earthing work & Testing | H4_Grid Earthing | F1.1.3; F1.2.2; F1.3.2; F1.4.2; F1.5.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.1.6
No Change | G.1.1 | Electrical | 150014478 | DC Network |  | DC Network - Equipment Installation & Testing and Cable Termination |  | String Inverter |  | Per Inverter | NO | G1.1.1 | Inverter Installation, Testing & Equipment Earthing |  | Inverter installation; Equipment body Earthing | H3_String Inverter Installation & Earthing | - |  | A.1.2
No Change | G.1.2 | Electrical | 150014478 | DC Network |  | DC Network - Equipment Installation & Testing and Cable Termination |  | String Inverter - LT Cable Termination |  | Per Inverter | NO | G1.2.1 | LT Cable Termination at Inverter |  | LT Cable Lugging, Crimping, Sleeving & Torquing | F3_ LT Cable Termination | F2.1.1; G1.1.1
No Change | G.1.3 | Electrical | 150014478 | DC Network |  | DC Network - Equipment Installation & Testing and Cable Termination |  | String Inverter - String Formation |  | Per Inverter | NO | G1.3.1 | MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing |  | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | H2_MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | -
No Change | G.2.1 | Electrical | 150014478 | DC Network |  | DC Network - Laying of Cable and Cable Management System |  | DC Cable Works |  | Per Inverter | M | G2.1.1 | Trench Excavation, DC Cable Laying, Dressing, Conduiting and PU Foam Sealing |  | Trench excavation, DC cable laying, dressing, conduiting (Modules to Inverter) | H1_Trench Excavation, DC Cable Laying and Conduiting | - |  |  |  | C.1.1
No Change | G.3.1 | Electrical | 150014478 | DC Network |  | DC Network - Earthing |  | Earthing of tables |  | Per Table | M | G3.1.1 | Table-to-Table & Grid Earthing Work Testing |  | Table-to-table & grid earthing work testing | H4_Grid Earthing | - |  |  | B.1.1
No Change | H.1.1 | Electrical | 150027433 | HT Cabling | HT Cabling | HT Cable Laying & Termination |  | HT cable - Pre-Laying |  | Block | KM | H.1.1.1 | HT Cable - Pre-Laying |  | i. Check the IR of the cable drum ii. Excavation of Trench iii. First layer of Sand Bedding | 16-HT Cable Field Quality Protocol (Pre-Laying Section) | -
No Change | H.1..1 | Electrical | 150027433 | HT Cabling | HT Cabling | HT Cable Laying & Termination |  | HT Cable - Laying and Termination |  | Block | KM | H.1.1.2a | HT Cable - Laying and Termination |  | i. Cable laying with proper routine ii. Bricks laying properly iii. Second layer sand bedding iv. Backfilling of trench also with FO cable and Caution Tap v. Check the cable straight through and End Termination Joints. vi. Checking of precast chamber (if applicable) | 16-HT Cable Field Quality Protocol (Laying Section) | H.1.1.1 |  |  |  | C.1.1
[12 empty] | H.1.1.2b | FO Cable - Laying and Termination |  | i. Final checking of FO cable laying, splicing and termination
No Change | H.1.1 | Electrical | 150027433 | HT Cabling | HT Cabling | HT Cable Laying & Termination |  | HT Cable - Testing |  | Block | KM | H.1.1.3 | HT Cable - Testing |  | i. VLF of the whole line Ii. Megger of Line | 16-HT Cable Field Quality Protocol (Pre-Commissioning Section) | H.1.1.2 |  |  | B.1.1
[14 empty] | 0-1km | 1.1km
[14 empty] | 1-2km | 1.2km
[14 empty] | 2-3km | 0.9km
[14 empty] | 3-4km | 1km
[14 empty] | 4-5km | 1km
Note on H5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on I5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on K5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on S5: Hemdeep Padalia: This will be used to sequence inspection checkpoints (within a sub-activity) and order of sub-activity in which RFI can be created
Note on O28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on P28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on S35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this
Note on S36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this - to be checked if both lift walls can be done in parallel
Note on S79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on S81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on S83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on S85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on R89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on S89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In addition to mentioned checkpoints, need to ask Kamalesh if there is any other pre-requisite Reply: Ok
Note on R90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on S91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Also include LT Cable Laying here - D2.1.1 Reply: Done Reply: Done
Note on R94: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained

## Activity-Checklist_08.11.25 (hidden)
AGEL CIVIL and ELECTRICAL Package > Sub-Package > Activity > Sub-Activity Structure along with Inspection Checklist Mapping
| As defined in PULSE+DRS Platform Master Data |  |  |  | To be selected by Contractor during creation of RFI | As per the SAP PO UoM
Sr. No. | Package | Sub-Package | Activity | Sub-Activity | Min. Unit of RFI (Per Table / Per Inverter / Per Block) | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checkpoint Code | Inspection Checkpoint Name | Inspection Checkpoint Description | Inspection Checklist Name | Is the Inspection Checkpoint Optional? | Preceding Inspection Checkpoint to be completed before raising RFI | Activity Dependency
[13 empty] | 1 | 2 | 3 | 4 | 5
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A.1.1.1
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A.1.1.2
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A.1.1.3
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A1.2.1
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.2.2
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.2.3
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A1.3.1
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.3.2
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.3.3
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A1.4.1
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.4.2
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.4.3
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | Y | - | -
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | Y | A2.1.1
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.3 | Pre Pour Inspection for Column & Slab - Cast-in-Situ | Fixing of reinforcements (as per BBS), positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Cordinates & Location of opening, cut-outs (Size as per drawing) upto concreting works (mixing & pouring). | C_1_Pour Card | N | A2.1.2
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.4 | Post Pour Inspection for Column & Slab - Cast-in-Situ | Physical Dimension of structure as per drawing & appearnce (free of defect, deformations, etc.,.) and curing etc. | C_8_Post Pour Check | N | A2.1.3
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.5 | Canopy Erection with Sheeting after Grouting | Fixing of nut & bolts in erected structure prior to final allignment check and tightening | C_11_Dimensional Assembly,Fitup Check Report and Inspection of Structural Alignment | N | A2.1.4
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.6 | Grouting | Readiness of grouting area (hacking, cleaning, soaking, shuttering,mixing,cube sampling works), grout pouring and acceptance of grout cube strength test results | C_34_Grouting Works | N | A2.1.5
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.2 | Gravel Filling | Filling of suitable size gravels / sand as per drawing (Approved source material, physically Tested as per SFQP & accepted by Quality) | C_27_Gravel Filling Works | N | A2.2.1
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.3 | Sand Relative Density Test | To check the relative density of sand | C_15_FDD Test by Sand Replacement Method | Y | A2.2.2
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.4 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying & finishing upto required level | C_36_PCC Works | N | A2.2.3
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.5 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and upto concreting works | C_1_Pour Card | N | A2.2.4
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.6 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.2.5
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.7 | Pre Pour Inspection for 1st Lift Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.6
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.8 | Post Pour Inspection for 1st Lift Wall | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.7
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.9 | Backfiling Layer Wise | Layer-wise filling, compaction & testing in each layer untill achieving accepted test result. | C_16_FDD Test by Core Cutter Method | N | A2.2.8
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.10 | Pre Pour Inspection for 2nd Lift Wall with Rail | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.9
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.11 | Post Pour Inspection for 2nd Lift Wall with Rail | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.10
A.2.3 | Civil |  | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | -
A.2.3 | Civil |  | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A.2.3.1
A.2.3 | Civil |  | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A.2.3.2
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.1 | Sub Grade Compaction Test & Leveling | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level | C_36_PCC Works | N | A2.4.1
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.3 | Pre Pour Inspection for RCC Block | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and concreting works | C_1_Pour Card | N | A2.4.2
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.4 | Post Pour Inspection for RCC Block | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.4.3
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.5.1
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.3 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | N | A2.5.2
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.4 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.5.3
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.1 | Levelling & Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.2 | Rubble Soling Test | Laying of requisite size rubble soling material upto compaction | C_27_Gravel Filling Works | N | A2.6.1
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.3 | Pre-Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.6.2
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.4 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | Y | A2.6.3
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.5 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) with rectifications if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.6.4
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.6 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | Y | A2.6.5
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.7 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.6.6
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.8 | Pre Pour Inspection for Slab | Fixing & tighntness of shuttering supports, leak-proof arranegments, Reinforcement fixing, positioning of pockets/inserts/embedments. And upto concreting works | C_1_Pour Card | Y | A2.6.7
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.9 | Post Pour Inspection for Slab | Surface level/slope & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectification of defects if any | C_8_Post Pour Check | Y | A2.6.8
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.10 | Leak Test, Rectification of Defects, Acceptance of Corrective Actions Taken (if applicable) | Leak Test | C_8_Post Pour Check | Y | A2.6.9
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.1 | Sub Grade Compaction Test (including Rubble Soiling) | Levelling & compaction test of base & Laying of rubble | C_16_FDD Test by Core Cutter Method | N | - | -
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.2 | Pre Pour Inspection for Sump PCC | Level & Grid Marking for PCC Laying & finishing upto required level and concreting works | C_36_PCC Works | N | A2.7.1
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.3 | Pre Pour Inspection for Sump Raft | Fixing of reinforcements as per drawing prior to shutter board fixing, positioning of inserts & embedments (if any) and concreting works | C_1_Pour Card | N | A2.7.2
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.4 | Post Pour Inspection for Sump Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.7.3
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.5 | Pre Pour Inspection for Dyke Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | N | A2.7.4
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.6 | Post Pour Inspection for Dyke Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | N | A2.7.5
B.1.1 | Civil | MMS Installation | MMS Installation | MMS Installation | Per Table | MT | B1.1.1 | MMS Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_1 MMS Installation Protocol- Fixed Tilt 2) C_29_1 MMS Installation Protocol - Tracker | N | A.1.1.3 |  | A.1.1
C.1.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Module Installation | Module Installation | Per Table | EA | C1.1.1 | Module Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_2 Module Installation Protocol- Fixed Tilt 2) C_29_2 Module Installation Protocol - Tracker | N | B1.1.1 |  |  | B.1.1
C.2.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of binders/clips, bridges, docking & reverse stations | Per Table | Not Applicable | C2.1.1 | Final Inspection of Alignment, Torquing of Docking Station, Flexible Bridge, Return Station | Inspection Checklist for Installation of Cleaning Robot Structures | 1) Cleaning Robot Installation Checklist_Leapting 2) Cleaning Robot Installation Checklist_Sol Bright 3) Cleaning Robot Installation Checklist_Airtouch | N | C1.1.1; A1.3.3 |  |  |  | C.1.1,A1.3,B1.1
C.3.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.1 | Fencing Pole Concrete Works Check | Markig of locations of posts, hole depth, Alignment, Verticality & level of Fence Post & concreting works as per drawing | C_47 USS,IDT,PSS Fencing Concrete Pole Works | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1; D2.1.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.1
C.3.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.2 | Fixing of Fencing Wire, Concertina, Gates as per drawing with Painting | Fixing of Fencing wire, concertina, Gates as per drawing with painting | C_10_Installation & Erection of Honey Comb Fence Post & Accessories | N | C3.1.1
C.3.2 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Gravel Laying | Block | Not Applicable | C3.2.1 | Gravel Filling | Inspection of Gravel Filling Works | C_27_Gravel Filling Works | N | C3.1.2 |  |  |  | C.3.1, D.1.6, D.2.1, D.2.3, D.3.1
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.1 | IDT and Accessories Installation | IDT Installation along with Accessories | A1_IDT and Accessories Installation | N | A2.2.11 |  | A.2.2
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.2 | IDT Electrical & Oil Filtration Testing | Electrical and Oil Filtration testing of IDT after installation | A2_IDT Oil Filled Transformer Oil Filtration and Testing + Upload of 3 testing reports | N | D1.1.1
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.3 | Inverter Cable Terminations & Equipment Earthing | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | A3_IDT Oil Filled Transformer HT, LT and Control Cable Termination, Equipment Earthing | N | D1.1.2
D.1.2 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.1 | HT Panel Installation & Testing | Panel installation and Panel testing | C1_HT Panel Installation & Testing + Upload of Testing Report | N | A2.1.6 |  | A.2.1
D.1.2 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.2 | HT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, HT cable end termination, Torquing, Equipment body Earthing | C2_Cable Termination & Equipment Body Earthing | N | D1.2.1
D.1.3 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.1 | LT Panel Installation & Testing | Panel installation and Panel testing | B1_LT Panel Installation & Testing + Upload of Testing Report | N | A2.1.6 |  | A.2.1
D.1.3 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.2 | LT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | B2_Cable Termination & Equipment Body Earthing | N | D1.3.1
D.1.4 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.1 | Auxiliary Transformer Installation & Testing | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | D1_Auxiliary Transformer Installation & Testing + Upload of Testing Report | N | A2.4.4 |  | A.2.3
D.1.4 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.2 | Auxiliary Transformer Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | D2_Cable Termination & Equipment Body Earthing | N | D1.4.1
D.1.5 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | NIFPS | Block | LOT | D1.5.1 | NIFPS Installation & Testing | NIFPS Installation & Testing | No Checklist; only testing report to be uploaded | Y | A2.5.4 |  | A.2.4
D.2.1 | Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Laying - Inverter to LT Panel | Per Inverter | M | D2.1.1 | Cable Drum IR Test and Cable Hanging for Above-Ground Section | Cable drum IR test and Cable hanging for above-ground section | F1_1 Cable Drum IR test, Cable Hanging | N | A1.4.4 |  |  | D.2.5
D.2.2 | Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Mgmt System Laying | Block | Not Applicable | D2.2.1 | Messenger Wire Hanging | Messenger wire hanging | F1_2 Messenger Wire Hanging | N | A1.4.4 |  | A.1.4
D.3.1 | Electrical | AC / LT Network | AC/LT Network - Earthing | Grid Earthing | Block | M | D3.1.1 | Grid Earthing Work & Testing | Grid Earthing work & Testing | H4_Grid Earthing | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.1.6
E.1.1 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter | Per Inverter | NO | E1.1.1 | Inverter Installation, Testing & Equipment Earthing | Inverter installation; Equipment body Earthing | H3_String Inverter Installation & Earthing | N | A1.2.3 |  | A.1.2
E.1.2 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - LT Cable Termination | Per Inverter | NO | E1.2.1 | LT Cable Termination at Inverter | LT Cable Lugging, Crimping, Sleeving & Torquing | F3_ LT Cable Termination | N | D2.1.1; E1.1.1
E.1.3 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - String Formation | Per Inverter | NO | E1.3.1 | MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | H2_MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | N | C1.1.1
E.2.1 | Electrical | DC Network | DC Network - Cable Laying | DC Cable Works | Per Inverter | M | E2.1.1 | Trench Excavation, DC Cable Laying, Dressing, Conduiting and PU Foam Sealing | Trench excavation, DC cable laying, dressing, conduiting (Modules to Inverter) | H1_Trench Excavation, DC Cable Laying and Conduiting | N | C1.1.1 |  |  |  | C.1.1
E.3.1 | Electrical | DC Network | DC Network - Earthing | Earthing of tables | Per Table | M | E3.1.1 | Table-to-Table & Grid Earthing Work Testing | Table-to-table & grid earthing work testing | H4_Grid Earthing | N | B1.1.1 |  |  | B.1.1
Note on E5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on H5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to validate by EoD Reply: Validated
Note on L5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to update document names Reply: Done
Note on M5: Hemdeep Padalia: For cases of "Y", a checkbox is required on Inspection Checkpoint screen like "Inspection check not required" (select button)
Note on N5: Hemdeep Padalia: This will be used to sequence inspection checkpoints (within a sub-activity) and order of sub-activity in which RFI can be created
Note on J30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on N37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this
Note on N38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this - to be checked if both lift walls can be done in parallel
Note on N69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Can remove B1.1.1 here since C1.1.1 is linked to it Reply: Done
Note on J72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on N72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be checked which are the pre-requisites
Note on N75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prerequisite(s) - LT Cable Hanging piling (A1.4), need to check if messenger wire hanging (D2.2.1)should be included here Reply: Okay, let’s keep only A1.4.4 for now
Note on L85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In addition to mentioned checkpoints, need to ask Kamalesh if there is any other pre-requisite Reply: Ok
Note on L86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A1.2.5 is not mandatory for completion before E1.1.1. However, for WMC generation, all activities need to be completed Reply: Aligned
Note on N87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Also include LT Cable Laying here - D2.1.1 Reply: Done Reply: Done
Note on N88: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prerequisite(s) - Module installation (C1.1.1) Reply: Done
Note on L90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N90: Hemdeep Padalia: Linkage to which preceding activity?

## Activity-Checklist_01.01.26
AGEL CIVIL and ELECTRICAL Package > Sub-Package > Activity > Sub-Activity Structure along with Inspection Checklist Mapping
| As defined in PULSE+DRS Platform Master Data |  |  |  | To be selected by Contractor during creation of RFI | As per the SAP PO UoM
Sr. No. | Package | Sub-Package | Activity | Sub-Activity | Min. Unit of RFI (Per Table / Per Inverter / Per Block) | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checkpoint Code | Inspection Checkpoint Name | Inspection Checkpoint Description | Inspection Checklist Name | Is the Inspection Checkpoint Optional? | Preceding Inspection Checkpoint to be completed before raising RFI | Activity Dependency |  |  |  |  | Remarks
[13 empty] | 1 | 2 | 3 | 4 | 5
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A.1.1.1
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A.1.1.2
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A.1.1.3
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A1.2.1
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.2.2
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.2.3
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A1.3.1
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.3.2
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.3.3
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A1.4.1
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.4.2
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.4.3
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | Y | - | -
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | Y | A2.1.1
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.3 | Pre Pour Inspection for Column & Slab - Cast-in-Situ | Fixing of reinforcements (as per BBS), positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Cordinates & Location of opening, cut-outs (Size as per drawing) upto concreting works (mixing & pouring). | C_1_Pour Card | N | A2.1.2
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.4 | Post Pour Inspection for Column & Slab - Cast-in-Situ | Physical Dimension of structure as per drawing & appearnce (free of defect, deformations, etc.,.) and curing etc. | C_8_Post Pour Check | N | A2.1.3
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.5 | Canopy Erection with Sheeting after Grouting | Fixing of nut & bolts in erected structure prior to final allignment check and tightening | C_11_Dimensional Assembly,Fitup Check Report and Inspection of Structural Alignment | N | A2.1.4
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.6 | Grouting | Readiness of grouting area (hacking, cleaning, soaking, shuttering,mixing,cube sampling works), grout pouring and acceptance of grout cube strength test results | C_34_Grouting Works | N | A2.1.5
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.2 | Gravel Filling | Filling of suitable size gravels / sand as per drawing (Approved source material, physically Tested as per SFQP & accepted by Quality) | C_27_Gravel Filling Works | N | A2.2.1
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.3 | Sand Relative Density Test | To check the relative density of sand | C_15_FDD Test by Sand Replacement Method | Y | A2.2.2
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.4 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying & finishing upto required level | C_36_PCC Works | N | A2.2.3
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.5 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and upto concreting works | C_1_Pour Card | N | A2.2.4
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.6 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.2.5
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.7 | Pre Pour Inspection for 1st Lift Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.6
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.8 | Post Pour Inspection for 1st Lift Wall | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.7
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.9 | Backfiling Layer Wise | Layer-wise filling, compaction & testing in each layer untill achieving accepted test result. | C_16_FDD Test by Core Cutter Method | N | A2.2.8
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.10 | Pre Pour Inspection for 2nd Lift Wall with Rail | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.9
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.11 | Post Pour Inspection for 2nd Lift Wall with Rail | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.10
A.2.3 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | -
A.2.3 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A.2.3.1
A.2.3 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A.2.3.2
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.1 | Sub Grade Compaction Test & Leveling | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level | C_36_PCC Works | N | A2.4.1
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.3 | Pre Pour Inspection for RCC Block | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and concreting works | C_1_Pour Card | N | A2.4.2
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.4 | Post Pour Inspection for RCC Block | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.4.3
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.5.1
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.3 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | N | A2.5.2
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.4 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.5.3
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.1 | Levelling & Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.2 | Rubble Soling Test | Laying of requisite size rubble soling material upto compaction | C_27_Gravel Filling Works | N | A2.6.1
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.3 | Pre-Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.6.2
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.4 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | Y | A2.6.3
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.5 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) with rectifications if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.6.4
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.6 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | Y | A2.6.5
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.7 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.6.6
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.8 | Pre Pour Inspection for Slab | Fixing & tighntness of shuttering supports, leak-proof arranegments, Reinforcement fixing, positioning of pockets/inserts/embedments. And upto concreting works | C_1_Pour Card | Y | A2.6.7
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.9 | Post Pour Inspection for Slab | Surface level/slope & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectification of defects if any | C_8_Post Pour Check | Y | A2.6.8
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.10 | Leak Test, Rectification of Defects, Acceptance of Corrective Actions Taken (if applicable) | Leak Test | C_8_Post Pour Check | Y | A2.6.9
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.1 | Sub Grade Compaction Test (including Rubble Soiling) | Levelling & compaction test of base & Laying of rubble | C_16_FDD Test by Core Cutter Method | N | - | -
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.2 | Pre Pour Inspection for Sump PCC | Level & Grid Marking for PCC Laying & finishing upto required level and concreting works | C_36_PCC Works | N | A2.7.1
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.3 | Pre Pour Inspection for Sump Raft | Fixing of reinforcements as per drawing prior to shutter board fixing, positioning of inserts & embedments (if any) and concreting works | C_1_Pour Card | N | A2.7.2
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.4 | Post Pour Inspection for Sump Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.7.3
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.5 | Pre Pour Inspection for Dyke Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | N | A2.7.4
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.6 | Post Pour Inspection for Dyke Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | N | A2.7.5
B.1.1 | Civil | MMS Installation | MMS Installation | MMS Installation | Per Table | MT | B1.1.1 | MMS Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_1 MMS Installation Protocol- Fixed Tilt 2) C_29_1 MMS Installation Protocol - Tracker | N | A.1.1.3 |  | A.1.1
C.1.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Module Installation | Module Installation | Per Table | EA | C1.1.1 | Module Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_2 Module Installation Protocol- Fixed Tilt 2) C_29_2 Module Installation Protocol - Tracker | N | B1.1.1 |  |  | B.1.1
C.2.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of binders/clips, bridges, docking & reverse stations | Per Table | Not Applicable | C2.1.1 | Final Inspection of Alignment, Torquing of Docking Station, Flexible Bridge, Return Station | Inspection Checklist for Installation of Cleaning Robot Structures | 1) Cleaning Robot Installation Checklist_Leapting 2) Cleaning Robot Installation Checklist_Sol Bright 3) Cleaning Robot Installation Checklist_Airtouch | N | C1.1.1; A1.3.3 |  |  |  | C.1.1,A1.3,B1.1
C.3.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.1 | Fencing Pole Concrete Works Check | Markig of locations of posts, hole depth, Alignment, Verticality & level of Fence Post & concreting works as per drawing | C_47 USS,IDT,PSS Fencing Concrete Pole Works | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1; D2.1.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.1
C.3.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.2 | Fixing of Fencing Wire, Concertina, Gates as per drawing with Painting | Fixing of Fencing wire, concertina, Gates as per drawing with painting | C_10_Installation & Erection of Honey Comb Fence Post & Accessories | N | C3.1.1
C.3.2 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Gravel Laying | Block | Not Applicable | C3.2.1 | Gravel Filling | Inspection of Gravel Filling Works | C_27_Gravel Filling Works | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1; D2.1.1 |  |  |  | C.3.1, D.1.6, D.2.1, D.2.3, D.3.1
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.1 | IDT and Accessories Installation | IDT Installation along with Accessories | A1_IDT and Accessories Installation | N | A2.2.11 |  | A.2.2
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.2 | IDT Electrical & Oil Filtration Testing | Electrical and Oil Filtration testing of IDT after installation | A2_IDT Oil Filled Transformer Oil Filtration and Testing + Upload of 3 testing reports | N | D1.1.1
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.3 | Inverter Cable Terminations & Equipment Earthing | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | A3_IDT Oil Filled Transformer HT, LT and Control Cable Termination, Equipment Earthing | N | D1.1.2
D.1.2 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.1 | HT Panel Installation & Testing | Panel installation and Panel testing | C1_HT Panel Installation & Testing + Upload of Testing Report | N | A2.1.6 |  | A.2.1
D.1.2 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.2 | HT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, HT cable end termination, Torquing, Equipment body Earthing | C2_Cable Termination & Equipment Body Earthing | N | D1.2.1
D.1.3 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.1 | LT Panel Installation & Testing | Panel installation and Panel testing | B1_LT Panel Installation & Testing + Upload of Testing Report | N | A2.1.6 |  | A.2.1
D.1.3 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.2 | LT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | B2_Cable Termination & Equipment Body Earthing | N | D1.3.1
D.1.4 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.1 | Auxiliary Transformer Installation & Testing | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | D1_Auxiliary Transformer Installation & Testing + Upload of Testing Report | N | A2.4.4 |  | A.2.3
D.1.4 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.2 | Auxiliary Transformer Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | D2_Cable Termination & Equipment Body Earthing | N | D1.4.1
D.1.5 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | NIFPS | Block | LOT | D1.5.1 | NIFPS Installation & Testing | NIFPS Installation & Testing | No Checklist; only testing report to be uploaded | Y | A2.5.4 |  | A.2.4
D.2.1 | Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Laying - Inverter to LT Panel | Per Inverter | M | D2.1.1 | Cable Drum IR Test and Cable Hanging for Above-Ground Section | Cable drum IR test and Cable hanging for above-ground section | F1_1 Cable Drum IR test, Cable Hanging | N | A1.4.4 |  |  | D.2.5
D.2.2 | Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Mgmt System Laying | Block | Not Applicable | D2.2.1 | Messenger Wire Hanging | Messenger wire hanging | F1_2 Messenger Wire Hanging | N | A1.4.4 |  | A.1.4
D.3.1 | Electrical | AC / LT Network | AC/LT Network - Earthing | Grid Earthing | Block | M | D3.1.1 | Grid Earthing Work & Testing | Grid Earthing work & Testing | H4_Grid Earthing | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.1.6
E.1.1 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter | Per Inverter | NO | E1.1.1 | Inverter Installation, Testing & Equipment Earthing | Inverter installation; Equipment body Earthing | H3_String Inverter Installation & Earthing | N | A1.2.3 |  | A.1.2
E.1.2 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - LT Cable Termination | Per Inverter | NO | E1.2.1 | LT Cable Termination at Inverter | LT Cable Lugging, Crimping, Sleeving & Torquing | F3_ LT Cable Termination | N | D2.1.1; E1.1.1
E.1.3 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - String Formation | Per Inverter | NO | E1.3.1 | MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | H2_MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | N | C1.1.1
E.2.1 | Electrical | DC Network | DC Network - Cable Laying | DC Cable Works | Per Inverter | M | E2.1.1 | Trench Excavation, DC Cable Laying, Dressing, Conduiting and PU Foam Sealing | Trench excavation, DC cable laying, dressing, conduiting (Modules to Inverter) | H1_Trench Excavation, DC Cable Laying and Conduiting | N | C1.1.1 |  |  |  | C.1.1
E.3.1 | Electrical | DC Network | DC Network - Earthing | Earthing of tables | Per Table | M | E3.1.1 | Table-to-Table & Grid Earthing Work Testing | Table-to-table & grid earthing work testing | H4_Grid Earthing | N | A.1.1.3 |  |  | B.1.1
E.4.1 | Electrical | AC / HT Network | HT Network - Cable Laying | HT Cable Laying - IDT to Feeder | Per Block | KM | E4.1.1
E.4.1 | Electrical | AC / HT Network | HT Network - Cable Laying | HT Cable Laying - IDT to Feeder | Per Block | KM | E4.1.1
E.4.1 | Electrical | AC / HT Network | HT Network - Cable Laying | HT Cable Laying - IDT to Feeder | Per Block | KM | E4.1.1
Note on E5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on H5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to validate by EoD Reply: Validated
Note on L5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to update document names Reply: Done
Note on M5: Hemdeep Padalia: For cases of "Y", a checkbox is required on Inspection Checkpoint screen like "Inspection check not required" (select button)
Note on N5: Hemdeep Padalia: This will be used to sequence inspection checkpoints (within a sub-activity) and order of sub-activity in which RFI can be created
Note on J30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on N37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this
Note on N38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this - to be checked if both lift walls can be done in parallel
Note on N69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Can remove B1.1.1 here since C1.1.1 is linked to it Reply: Done
Note on J72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on N75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prerequisite(s) - LT Cable Hanging piling (A1.4), need to check if messenger wire hanging (D2.2.1)should be included here Reply: Okay, let’s keep only A1.4.4 for now
Note on L85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In addition to mentioned checkpoints, need to ask Kamalesh if there is any other pre-requisite Reply: Ok
Note on L86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A1.2.5 is not mandatory for completion before E1.1.1. However, for WMC generation, all activities need to be completed Reply: Aligned
Note on N87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Also include LT Cable Laying here - D2.1.1 Reply: Done Reply: Done
Note on N88: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prerequisite(s) - Module installation (C1.1.1) Reply: Done
Note on L90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained

## Activity-Checklist_19.11.2025 (hidden)
AGEL CIVIL and ELECTRICAL Package > Sub-Package > Activity > Sub-Activity Structure along with Inspection Checklist Mapping
| As defined in PULSE+DRS Platform Master Data |  |  |  | To be selected by Contractor during creation of RFI | As per the SAP PO UoM
Sr. No. | Package | Sub-Package | Activity | Sub-Activity | Min. Unit of RFI (Per Table / Per Inverter / Per Block) | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checkpoint Code | Inspection Checkpoint Name | Inspection Checkpoint Description | Inspection Checklist Name | Is the Inspection Checkpoint Optional? | Preceding Inspection Checkpoint to be completed before raising RFI | Activity Dependency |  |  |  |  | Remarks
[13 empty] | 1 | 2 | 3 | 4 | 5
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A.1.1.1
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A.1.1.2
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A.1.1.3
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A1.2.1
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.2.2
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.2.3
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A1.3.1
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.3.2
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.3.3
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | - | -
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A1.4.1
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.4.2
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.4 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.4.3
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | Y | - | -
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | Y | A2.1.1
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.3 | Pre Pour Inspection for Column & Slab - Cast-in-Situ | Fixing of reinforcements (as per BBS), positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Cordinates & Location of opening, cut-outs (Size as per drawing) upto concreting works (mixing & pouring). | C_1_Pour Card | N | A2.1.2
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.4 | Post Pour Inspection for Column & Slab - Cast-in-Situ | Physical Dimension of structure as per drawing & appearnce (free of defect, deformations, etc.,.) and curing etc. | C_8_Post Pour Check | N | A2.1.3
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.5 | Canopy Erection with Sheeting after Grouting | Fixing of nut & bolts in erected structure prior to final allignment check and tightening | C_11_Dimensional Assembly,Fitup Check Report and Inspection of Structural Alignment | N | A2.1.4
A.2.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.6 | Grouting | Readiness of grouting area (hacking, cleaning, soaking, shuttering,mixing,cube sampling works), grout pouring and acceptance of grout cube strength test results | C_34_Grouting Works | N | A2.1.5
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.2 | Gravel Filling | Filling of suitable size gravels / sand as per drawing (Approved source material, physically Tested as per SFQP & accepted by Quality) | C_27_Gravel Filling Works | N | A2.2.1
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.3 | Sand Relative Density Test | To check the relative density of sand | C_15_FDD Test by Sand Replacement Method | Y | A2.2.2
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.4 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying & finishing upto required level | C_36_PCC Works | N | A2.2.3
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.5 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and upto concreting works | C_1_Pour Card | N | A2.2.4
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.6 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.2.5
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.7 | Pre Pour Inspection for 1st Lift Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.6
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.8 | Post Pour Inspection for 1st Lift Wall | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.7
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.9 | Backfiling Layer Wise | Layer-wise filling, compaction & testing in each layer untill achieving accepted test result. | C_16_FDD Test by Core Cutter Method | N | A2.2.8
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.10 | Pre Pour Inspection for 2nd Lift Wall with Rail | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.9
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.11 | Post Pour Inspection for 2nd Lift Wall with Rail | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.10
A.2.3 | Civil |  | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.1 | Pre Pour Inspection - Pile | Grid Marking & Cordinate Checking, Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wire, Concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_1 Micro Pile Checklist | N | -
A.2.3 | Civil |  | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.2 | Pre Pour Inspection - Pile Cap | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_14_2 Micro Pile Cap Checklist | N | A.2.3.1
A.2.3 | Civil |  | IDT Civil & Structural | IDT Civil & Structural - Cable Rack | Block | Not Applicable | A.2.3.3 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A.2.3.2
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.1 | Sub Grade Compaction Test & Leveling | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level | C_36_PCC Works | N | A2.4.1
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.3 | Pre Pour Inspection for RCC Block | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and concreting works | C_1_Pour Card | N | A2.4.2
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.4.4 | Post Pour Inspection for RCC Block | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.4.3
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.5.1
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.3 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | N | A2.5.2
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.5.4 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.5.3
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.1 | Levelling & Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.2 | Rubble Soling Test | Laying of requisite size rubble soling material upto compaction | C_27_Gravel Filling Works | N | A2.6.1
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.3 | Pre-Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.6.2
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.4 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | Y | A2.6.3
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.5 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) with rectifications if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.6.4
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.6 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | Y | A2.6.5
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.7 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.6.6
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.8 | Pre Pour Inspection for Slab | Fixing & tighntness of shuttering supports, leak-proof arranegments, Reinforcement fixing, positioning of pockets/inserts/embedments. And upto concreting works | C_1_Pour Card | Y | A2.6.7
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.9 | Post Pour Inspection for Slab | Surface level/slope & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectification of defects if any | C_8_Post Pour Check | Y | A2.6.8
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.6.10 | Leak Test, Rectification of Defects, Acceptance of Corrective Actions Taken (if applicable) | Leak Test | C_8_Post Pour Check | Y | A2.6.9
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.1 | Sub Grade Compaction Test (including Rubble Soiling) | Levelling & compaction test of base & Laying of rubble | C_16_FDD Test by Core Cutter Method | N | - | -
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.2 | Pre Pour Inspection for Sump PCC | Level & Grid Marking for PCC Laying & finishing upto required level and concreting works | C_36_PCC Works | N | A2.7.1
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.3 | Pre Pour Inspection for Sump Raft | Fixing of reinforcements as per drawing prior to shutter board fixing, positioning of inserts & embedments (if any) and concreting works | C_1_Pour Card | N | A2.7.2
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.4 | Post Pour Inspection for Sump Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.7.3
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.5 | Pre Pour Inspection for Dyke Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | N | A2.7.4
A.2.7 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.7.6 | Post Pour Inspection for Dyke Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | N | A2.7.5
B.1.1 | Civil | MMS Installation | MMS Installation | MMS Installation | Per Table | MT | B1.1.1 | MMS Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_1 MMS Installation Protocol- Fixed Tilt 2) C_29_1 MMS Installation Protocol - Tracker | N | A.1.1.3 |  | A.1.1
C.1.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Module Installation | Module Installation | Per Table | EA | C1.1.1 | Module Installation and Assembly | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_2 Module Installation Protocol- Fixed Tilt 2) C_29_2 Module Installation Protocol - Tracker | N | B1.1.1 |  |  | B.1.1
C.2.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of binders/clips, bridges, docking & reverse stations | Per Table | Not Applicable | C2.1.1 | Final Inspection of Alignment, Torquing of Docking Station, Flexible Bridge, Return Station | Inspection Checklist for Installation of Cleaning Robot Structures | 1) Cleaning Robot Installation Checklist_Leapting 2) Cleaning Robot Installation Checklist_Sol Bright 3) Cleaning Robot Installation Checklist_Airtouch | N | C1.1.1; A1.3.3 |  |  |  | C.1.1,A1.3,B1.1
C.3.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.1 | Fencing Pole Concrete Works Check | Markig of locations of posts, hole depth, Alignment, Verticality & level of Fence Post & concreting works as per drawing | C_47 USS,IDT,PSS Fencing Concrete Pole Works | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1; D2.1.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.1
C.3.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.2 | Fixing of Fencing Wire, Concertina, Gates as per drawing with Painting | Fixing of Fencing wire, concertina, Gates as per drawing with painting | C_10_Installation & Erection of Honey Comb Fence Post & Accessories | N | C3.1.1
C.3.2 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Gravel Laying | Block | Not Applicable | C3.2.1 | Gravel Filling | Inspection of Gravel Filling Works | C_27_Gravel Filling Works | N | C3.1.2 |  |  |  | C.3.1, D.1.6, D.2.1, D.2.3, D.3.1 |  | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1; D2.1.1
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.1 | IDT and Accessories Installation | IDT Installation along with Accessories | A1_IDT and Accessories Installation | N | A2.2.11 |  | A.2.2
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.2 | IDT Electrical & Oil Filtration Testing | Electrical and Oil Filtration testing of IDT after installation | A2_IDT Oil Filled Transformer Oil Filtration and Testing + Upload of 3 testing reports | N | D1.1.1
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.3 | Inverter Cable Terminations & Equipment Earthing | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | A3_IDT Oil Filled Transformer HT, LT and Control Cable Termination, Equipment Earthing | N | D1.1.2
D.1.2 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.1 | HT Panel Installation & Testing | Panel installation and Panel testing | C1_HT Panel Installation & Testing + Upload of Testing Report | N | A2.1.6 |  | A.2.1
D.1.2 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.2 | HT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, HT cable end termination, Torquing, Equipment body Earthing | C2_Cable Termination & Equipment Body Earthing | N | D1.2.1
D.1.3 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.1 | LT Panel Installation & Testing | Panel installation and Panel testing | B1_LT Panel Installation & Testing + Upload of Testing Report | N | A2.1.6 |  | A.2.1
D.1.3 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.2 | LT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | B2_Cable Termination & Equipment Body Earthing | N | D1.3.1
D.1.4 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.1 | Auxiliary Transformer Installation & Testing | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | D1_Auxiliary Transformer Installation & Testing + Upload of Testing Report | N | A2.4.4 |  | A.2.3
D.1.4 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.2 | Auxiliary Transformer Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | D2_Cable Termination & Equipment Body Earthing | N | D1.4.1
D.1.5 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | NIFPS | Block | LOT | D1.5.1 | NIFPS Installation & Testing | NIFPS Installation & Testing | No Checklist; only testing report to be uploaded | Y | A2.5.4 |  | A.2.4
D.2.1 | Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Laying - Inverter to LT Panel | Per Inverter | M | D2.1.1 | Cable Drum IR Test and Cable Hanging for Above-Ground Section | Cable drum IR test and Cable hanging for above-ground section | F1_1 Cable Drum IR test, Cable Hanging | N | A1.4.4 |  |  | D.2.5
D.2.2 | Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Mgmt System Laying | Block | Not Applicable | D2.2.1 | Messenger Wire Hanging | Messenger wire hanging | F1_2 Messenger Wire Hanging | N | A1.4.4 |  | A.1.4
D.3.1 | Electrical | AC / LT Network | AC/LT Network - Earthing | Grid Earthing | Block | M | D3.1.1 | Grid Earthing Work & Testing | Grid Earthing work & Testing | H4_Grid Earthing | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.1.6
E.1.1 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter | Per Inverter | NO | E1.1.1 | Inverter Installation, Testing & Equipment Earthing | Inverter installation; Equipment body Earthing | H3_String Inverter Installation & Earthing | N | A1.2.3 |  | A.1.2
E.1.2 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - LT Cable Termination | Per Inverter | NO | E1.2.1 | LT Cable Termination at Inverter | LT Cable Lugging, Crimping, Sleeving & Torquing | F3_ LT Cable Termination | N | D2.1.1; E1.1.1
E.1.3 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - String Formation | Per Inverter | NO | E1.3.1 | MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | H2_MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | N | C1.1.1
E.2.1 | Electrical | DC Network | DC Network - Cable Laying | DC Cable Works | Per Inverter | M | E2.1.1 | Trench Excavation, DC Cable Laying, Dressing, Conduiting and PU Foam Sealing | Trench excavation, DC cable laying, dressing, conduiting (Modules to Inverter) | H1_Trench Excavation, DC Cable Laying and Conduiting | N | C1.1.1 |  |  |  | C.1.1
E.3.1 | Electrical | DC Network | DC Network - Earthing | Earthing of tables | Per Table | M | E3.1.1 | Table-to-Table & Grid Earthing Work Testing | Table-to-table & grid earthing work testing | H4_Grid Earthing | N | B1.1.1 |  |  | B.1.1 |  |  | Link to A.1.1.3
Note on E5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on H5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to validate by EoD Reply: Validated
Note on L5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to update document names Reply: Done
Note on M5: Hemdeep Padalia: For cases of "Y", a checkbox is required on Inspection Checkpoint screen like "Inspection check not required" (select button)
Note on N5: Hemdeep Padalia: This will be used to sequence inspection checkpoints (within a sub-activity) and order of sub-activity in which RFI can be created
Note on J30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on N37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this
Note on N38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this - to be checked if both lift walls can be done in parallel
Note on N69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Can remove B1.1.1 here since C1.1.1 is linked to it Reply: Done
Note on J72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on N72: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be checked which are the pre-requisites
Note on N75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N77: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N79: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N83: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prerequisite(s) - LT Cable Hanging piling (A1.4), need to check if messenger wire hanging (D2.2.1)should be included here Reply: Okay, let’s keep only A1.4.4 for now
Note on L85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N85: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In addition to mentioned checkpoints, need to ask Kamalesh if there is any other pre-requisite Reply: Ok
Note on L86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A1.2.5 is not mandatory for completion before E1.1.1. However, for WMC generation, all activities need to be completed Reply: Aligned
Note on N87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Also include LT Cable Laying here - D2.1.1 Reply: Done Reply: Done
Note on N88: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prerequisite(s) - Module installation (C1.1.1) Reply: Done
Note on L90: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N90: Hemdeep Padalia: Linkage to which preceding activity?

## Activity-Checklist_09.10.25 (hidden)
AGEL CIVIL and ELECTRICAL Package > Sub-Package > Activity > Sub-Activity Structure along with Inspection Checklist Mapping
| As defined in PULSE+DRS Platform Master Data |  |  |  | To be selected by Contractor during creation of RFI | As per the SAP PO UoM
Sr. No. | Package | Sub-Package | Activity | Sub-Activity | Min. Unit of RFI (Per Table / Per Inverter / Per Block) | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checkpoint Code | Inspection Checkpoint Name | Inspection Checkpoint Description | Inspection Checklist Name | Is the Inspection Checkpoint Optional? | Preceding Inspection Checkpoint | Activity Dependency
[13 empty] | 1 | 2 | 3 | 4 | 5
A.1.1 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | A.1.1.1 | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | 1) C_9_1 Micro Pile Checklist of Fixed Tilt Structures 2) C_14_1 Micro Pile Checklist of Tracker Structures | N | - | -
[7 empty] | A.1.1.2 | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | 1) C_9_2 Micro Pile Checklist of Fixed Tilt Structures 2) C_14_2 Micro Pile Checklist of Tracker Structures | N | A.1.1.1
[7 empty] | A.1.1.3 | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | 1) C_9_2 Micro Pile Checklist of Fixed Tilt Structures 2) C_14_2 Micro Pile Checklist of Tracker Structures | N | A.1.1.2
[7 empty] | A.1.1.4 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A.1.1.3
[7 empty] | A.1.1.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A.1.1.4
A.1.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | A1.2.1 | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 Micro Pile Checklist of Fixed Tilt Structures | N | - | -
[7 empty] | A1.2.2 | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.2.1
[7 empty] | A1.2.3 | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.2.2
[7 empty] | A1.2.4 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.2.3
[7 empty] | A1.2.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.2.4
A.1.3 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Piling - Robotic Docking System | Piling - Robotic Docking System | Per Table | EA | A1.3.1 | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 Micro Pile Checklist of Fixed Tilt Structures | N | - | -
[7 empty] | A1.3.2 | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.3.1
[7 empty] | A1.3.3 | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.3.2
[7 empty] | A1.3.4 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.3.3
[7 empty] | A1.3.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.3.4
A.1.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Per Inverter | EA | A1.4.1 | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 Micro Pile Checklist of Fixed Tilt Structures | N | - | -
[7 empty] | A1.4.2 | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.4.1
[7 empty] | A1.4.3 | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | N | A1.4.2
[7 empty] | A1.4.4 | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8_Post Pour Check | N | A1.4.3
[7 empty] | A1.4.5 | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N | A1.4.4
A.2.1 | Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | A2.1.1 | Pre Pour Inspection for Micro Piling - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 Micro Pile Checklist of Fixed Tilt Structures | Y | - | -
[7 empty] | A2.1.2 | Pre Pour Inspection for Micro Piling - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Checking of pile cage, Top level of cage, cover, preparation of starter and concrete pouring works. Concreting Works (Mixing points), if mixing thorugh Ajax Floori (not required for RMC) | C_9_2 Micro Pile Checklist of Fixed Tilt Structures | Y | A2.1.1
[7 empty] | A2.1.3 | Pre Pour Inspection for Column & Slab - Cast-in-Situ | Fixing of reinforcements (as per BBS), positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Cordinates & Location of opening, cut-outs (Size as per drawing) upto concreting works (mixing & pouring). | C_1_Pour Card | N | A2.1.2
[7 empty] | A2.1.4 | Post Pour Inspection for Column & Slab - Cast-in-Situ | Physical Dimension of structure as per drawing & appearnce (free of defect, deformations, etc.,.) and curing etc. | C_8_Post Pour Check | N | A2.1.3
[7 empty] | A2.1.5 | Canopy Erection with Sheeting after grouting | Fixing of nut & bolts in erected structure prior to final allignment check and tightening | C_11_Dimensional Assembly,Fitup Check Report and Inspection of Structural Alignme | N | A2.1.4
[7 empty] | A2.1.6 | Grouting | Readiness of grouting area (hacking, cleaning, soaking, shuttering,mixing,cube sampling works), grout pouring and acceptance of grout cube strength test results | C_34_Grouting Works | N | A2.1.5
A.2.2 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | A2.2.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
[7 empty] | A2.2.2 | Gravel filling | Filling of suitable size gravels / sand as per drawing (Approved source material, physically Tested as per SFQP & accepted by Quality) | C_27_Gravel Filling Works | N | A2.2.1
[7 empty] | A2.2.3 | Sand Relative Density Test | To check the relative density of sand | C_15_FDD Test by Sand Replacement Method | Y | A2.2.2
[7 empty] | A2.2.4 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying & finishing upto required level | C_36_PCC Works | N | A2.2.3
[7 empty] | A2.2.5 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and upto concreting works | C_1_Pour Card | N | A2.2.4
[7 empty] | A2.2.6 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.2.5
[7 empty] | A2.2.7 | Pre Pour Inspection for Ist Lift Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.6
[7 empty] | A2.2.8 | Post Pour Inspection for Ist Lift Wall | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.7
[7 empty] | A2.2.9 | Backfiling Layer Wise | Layer-wise filling, compaction & testing in each layer untill achieving accepted test result. | C_16_FDD Test by Core Cutter Method | N | A2.2.8
[7 empty] | A2.2.10 | Pre Pour Inspection for 2nd Lift Wall with Rail | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1_Pour Card | N | A2.2.9
[7 empty] | A2.2.11 | Post Pour Inspection for 2nd Lift Wall with Rail | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8_Post Pour Check | N | A2.2.10
A.2.3 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | A2.3.1 | Sub Grade Compaction Test & Leveling | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
[7 empty] | A2.3.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level | C_36_PCC Works | N | A2.3.1
[7 empty] | A2.3.3 | Pre Pour Inspection for RCC Block | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and concreting works | C_1_Pour Card | N | A2.3.2
[7 empty] | A2.3.4 | Post Pour Inspection for RCC Block | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.3.3
A.2.4 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | A2.4.1 | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
[7 empty] | A2.4.2 | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.4.1
[7 empty] | A2.4.3 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | N | A2.4.2
[7 empty] | A2.4.4 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.4.3
A.2.5 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | A2.5.1 | Levelling & Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16_FDD Test by Core Cutter Method | Y | - | -
[7 empty] | A2.5.2 | Rubble Soling Test | Laying of requisite size rubble soling material upto compaction | C_27_Gravel Filling Works | N | A2.5.1
[7 empty] | A2.5.3 | Pre-pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36_PCC Works | N | A2.5.2
[7 empty] | A2.5.4 | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1_Pour Card | Y | A2.5.3
[7 empty] | A2.5.5 | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) with rectifications if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.5.4
[7 empty] | A2.5.6 | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | Y | A2.5.5
[7 empty] | A2.5.7 | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | Y | A2.5.6
[7 empty] | A2.5.8 | Pre Pour Inspection for Slab | Fixing & tighntness of shuttering supports, leak-proof arranegments, Reinforcement fixing, positioning of pockets/inserts/embedments. And upto concreting works | C_1_Pour Card | Y | A2.5.7
[7 empty] | A2.5.9 | Post Pour Inspection for Slab | Surface level/slope & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectification of defects if any | C_8_Post Pour Check | Y | A2.5.8
[7 empty] | A2.5.10 | Leak Test (If any), Rectification of defects (if any) & Acceptance of corrections action taken | Leak Test | C_8_Post Pour Check | Y | A2.5.9
A.2.6 | Civil | Piling (MMS, Inverter, LT Cable Hangers) + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | A2.6.1 | Sub Grade Compaction Test (including rubble soiling) | Levelling & compaction test of base & Laying of rubble | C_16_FDD Test by Core Cutter Method | N | - | -
[7 empty] | A2.6.2 | Pre Pour Inspection for Sump PCC | Level & Grid Marking for PCC Laying & finishing upto required level and concreting works | C_36_PCC Works | N | A2.6.1
[7 empty] | A2.6.3 | Pre Pour Inspection for Sump Raft | Fixing of reinforcements as per drawing prior to shutter board fixing, positioning of inserts & embedments (if any) and concreting works | C_1_Pour Card | N | A2.6.2
[7 empty] | A2.6.4 | Post Pour Inspection for Sump Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8_Post Pour Check | N | A2.6.3
[7 empty] | A2.6.5 | Pre Pour Inspection for Dyke Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1_Pour Card | N | A2.6.4
[7 empty] | A2.6.6 | Post Pour Inspection for Dyke Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8_Post Pour Check | N | A2.6.5
B.1.1 | Civil | MMS Installation | MMS Installation | MMS Installation | Per Table | MT | B1.1.1 | If Tracker: Tracker Alignment, Tightening & Torquing up to Torque Tube incl. Transmission Shaft If Fixed Tilt: Fixed Tilt Alignment, Tightening & Torquing up to bracing, perlin and all asembly parts | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_1 PV Module Mounting Structure Installation Protocol- Fixed Tilt 2) C_29_1 PV Module Mounting Structure Installation Protocol - Tracker | N | A.1.1.4 |  | A.1.1
C.1.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Module Installation | Module Installation | Per Table | EA | C1.1.1 | If Tracker: Tracker: Module Alignment, Tightening & Torquing incl. U bolt & purlin If Fixed Tilt: Fixed Tilt: Module Alignment, Tightening & Torquing incl. purline | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | 1) C_28_2PV Module Installation Protocol- Fixed Tilt 2) C_29_2 PV Module Installation Protocol - Tracker | N | B1.1.1 |  |  | B.1.1
C.2.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of binders/clips, bridges, docking & reverse stations | Per Table | Not Applicable | C2.1.1 | Final Inspection of alignment, torquing of docking station, Flexible bridge, return station | Inspection Checklist for Installation of Cleaning Robot Structures | 1) Cleaning Robot Installation Checklist_Leapting 2) Cleaning Robot Installation Checklist_Sol Bright 3) Cleaning Robot Installation Checklist_Airtouch | N | C1.1.1; A1.3.4 |  |  |  | C.1.1,A1.3,B1.1
C.3.1 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | C3.1.1 | Fencing pole concrete | Markig of locations of posts, hole depth, Alignment, Verticality & level of Fence Post & concreting works as per drawing | C_47 USS,IDT.PSS Fencing Concrete Pole Works | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1; D2.1.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.1
[7 empty] | C3.1.2 | Fixing of Fencing wire, concertina, Gates as per drawing with painting | Fixing of Fencing wire, concertina, Gates as per drawing with painting | C_10_Installation & Erection of Honey Comb Fence Post & Accessories | N | C3.1.1
C.3.2 | Civil | Module Installation, Robot Works, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Gravel Laying | Block | Not Applicable | C3.2.1 | Gravel filling | Inspection of Gravel Filling Works | C_27_Gravel Filling Works | N | C3.1.2 |  |  |  | C.3.1, D.1.6, D.2.1, D.2.3, D.3.1
D.1.1 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Transformer | Block | SET | D1.1.1 | IDT and Accessories Installation | IDT Installation along with Accessories | A1_IDT and Accessories Installation | N | A2.2.11 |  | A.2.2
[7 empty] | D1.1.2 | IDT Electrical & Oil Filtration Testing | Electrical and Oil Filtration testing of IDT after installation | A2_IDT Oil Filled Transformer Oil Filtration and Testing + Upload of 3 testing reports | N | D1.1.1
[7 empty] | D1.1.3 | Inverter Cable Terminations & Equipment Earthing | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | A3_IDT Oil Filled Transformer HT, LT and Control Cable Termination, Equipment Earthing | N | D1.1.2
D.1.2 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | HT Panel | Block | EA | D1.2.1 | HT Panel Installation & Testing | Panel installation and Panel testing | C1_HT Panel Installation & Testing + Upload of Testing Report | N | A2.1.6 |  | A.2.1
[7 empty] | D1.2.2 | HT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, HT cable end termination, Torquing, Equipment body Earthing | C2_Cable Termination & Equipment Body Earthing | N | D1.2.1
D.1.3 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | LT Panel | Block | NO | D1.3.1 | LT Panel Installation & Testing | Panel installation and Panel testing | B1_LT Panel Installation & Testing + Upload of Testing Report | N | A2.1.6 |  | A.2.1
[7 empty] | D1.3.2 | LT Panel Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | B2_Cable Termination & Equipment Body Earthing | N | D1.3.1
D.1.4 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | Auxiliary Transformer | Block | SET | D1.4.1 | Auxiliary Transformer Installation & Testing | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | D1_Auxiliary Transformer Installation & Testing + Upload of Testing Report | N | A2.3.4 |  | A.2.3
[7 empty] | D1.4.2 | Auxiliary Transformer Cable Terminations & Equipment Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | D2_Cable Termination & Equipment Body Earthing | N | D1.4.1
D.1.5 | Electrical | AC / LT Network | AC/LT Network - Equipment Installation & Testing and Cable Termination | NIFPS | Block | LOT | D1.5.1 | NIFPS Installation & Testing | NIFPS Installation & Testing | No Checklist; only testing report to be uploaded | Y | A2.4.4 |  | A.2.4
D.2.1 | Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Laying - Inverter to LT Panel | Per Inverter | M | D2.1.1 | Cable drum IR test and Cable hanging for above-ground section | Cable drum IR test and Cable hanging for above-ground section | F1_1 Cable Drum IR test, Cable Hanging | N | A1.4.4 |  |  | D.2.5
D.2.2 | Electrical | AC / LT Network | AC/LT Network - Cable & Cable Management System Laying | LT Cable Mgmt System Laying | Block | Not Applicable | D2.2.1 | Messenger wire hanging | Messenger wire hanging | F1_2 Messenger Wire Hanging | N | A1.4.4 |  | A.1.4
D.3.1 | Electrical | AC / LT Network | AC/LT Network - Earthing | Grid Earthing | Block | M | D3.1.1 | Grid Earthing work & Testing | Grid Earthing work & Testing | H4_Grid Earthing | N | D1.1.3; D1.2.2; D1.3.2; D1.4.2; D1.5.1 |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.1.6
E.1.1 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter | Per Inverter | NO | E1.1.1 | Inverter Installation, Testing & Equipment Earthing | Inverter installation; Equipment body Earthing | H3_String Inverter Installation & Earthing | N | A1.2.4 |  | A.1.2
E.1.2 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - LT Cable Termination | Per Inverter | NO | E1.2.1 | LT Cable termination at inverter | LT Cable Lugging, Crimping, Sleeving & Torquing | F3_ LT Cable Termination | N | D2.1.1; E1.1.1
E.1.3 | Electrical | DC Network | DC Network - Equipment Installation & Testing and Cable Termination | String Inverter - String Formation | Per Inverter | NO | E1.3.1 | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | H2_MC4 Connection, VOC Testing, Cable Dressing, Ferrule Checking and PU Foam Sealing | N | C1.1.1
E.2.1 | Electrical | DC Network | DC Network - Cable Laying | DC Cable Works | Per Inverter | M | E2.1.1 | Trench excavation, DC cable laying, dressing, conduiting and PU foam sealing | Trench excavation, DC cable laying, dressing, conduiting (Modules to Inverter) | H1_Trench Excavation, DC Cable Laying and Conduiting | N | C1.1.1 |  |  |  | C.1.1
E.3.1 | Electrical | DC Network | DC Network - Earthing | Earthing of tables | Per Table | M | E3.1.1 | Table-to-table & grid earthing work testing | Table-to-table & grid earthing work testing | H4_Grid Earthing | N | B1.1.1 |  |  | B.1.1
Note on E5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on H5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to validate by EoD Reply: Validated
Note on L5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to update document names Reply: Done
Note on M5: Hemdeep Padalia: For cases of "Y", a checkbox is required on Inspection Checkpoint screen like "Inspection check not required" (select button)
Note on N5: Hemdeep Padalia: This will be used to sequence inspection checkpoints (within a sub-activity) and order of sub-activity in which RFI can be created
Note on J27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Which checklist to use - C_9 and C_14 are for MMS piling and not HT/LT platform? Reply: Keeping only C_9 checklists (the once for Fixed Tilt which seems relevant)
Note on J34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on N41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this
Note on N42: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not sure about this - to be checked if both lift walls can be done in parallel
Note on N68: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A1.1.5 is not mandatory for completion before B1.1.1. However, for WMC generation, all activities need to be completed Reply: Aligned
Note on N70: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Can remove B1.1.1 here since C1.1.1 is linked to it Reply: Done
Note on J73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on N73: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: To be checked which are the pre-requisites
Note on N76: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N80: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N82: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Caveat to note: today, we are not locking these to the LT cable laying activity today because we are not capturing the end-to-end cable laying activity through RFIs - only the inverter-to-LT panel portion is being captured. If / when we have RFIs for cable laying within the IDT station, we can lock these RFIs to the completion of cable-laying. Reply: Yes
Note on N84: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prerequisite(s) - LT Cable Hanging piling (A1.4), need to check if messenger wire hanging (D2.2.1)should be included here Reply: Okay, let’s keep only A1.4.4 for now
Note on L86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N86: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In addition to mentioned checkpoints, need to ask Kamalesh if there is any other pre-requisite Reply: Ok
Note on L87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained
Note on N87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: A1.2.5 is not mandatory for completion before E1.1.1. However, for WMC generation, all activities need to be completed Reply: Aligned
Note on N88: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Also include LT Cable Laying here - D2.1.1 Reply: Done Reply: Done
Note on N89: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Prerequisite(s) - Module installation (C1.1.1) Reply: Done
Note on L91: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Checklist to obtained from user Reply: Obtained

## Activity-Checklist_03.10.25 (hidden)
AGEL CIVIL and ELECTRICAL Package > Sub-Package > Activity > Sub-Activity Structure along with Inspection Checklist Mapping
|  | As defined in PULSE+DRS Platform Master Data |  |  |  |  | To be selected by Contractor during creation of RFI | As per the SAP PO UoM
Sr. No. | Service Order | Package | Service Code | Sub-Package | Activity | Sub-Activity | Min. Unit of RFI (Per Table / Per Inverter / Per Block) | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checkpoints | Inspection Checkpoint Description | Inspection Checklist Number | Is the Checklist Optional? | Remarks | Activity Dependency
[14 empty] | 1 | 2 | 3 | 4 | 5
A.1.1 |  | Civil |  | Piling + IDT Civil & Structural | Piling - MMS | Piling - MMS | Per Table | EA | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | 1) Piling for Fixed Tilt MMS: C_9_1 2) Piling for Tracker MMS: C_14_1 | N |  | -
[9 empty] | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | 1) Piling for Fixed Tilt MMS: C_9_2 2) Piling for Tracker MMS: C_14_2 | N
[9 empty] | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | 1) Piling for Fixed Tilt MMS: C_9_2 2) Piling for Tracker MMS: C_14_2 | N
[9 empty] | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8 | N
[9 empty] | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N
A.1.2 |  | Civil |  | Piling + IDT Civil & Structural | Piling - Inverter | Piling - Inverter | Per Inverter | EA | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 | N |  | -
[9 empty] | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 | N
[9 empty] | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 | N
[9 empty] | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8 | N
[9 empty] | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N
A.1.3 |  | Civil |  | Piling + IDT Civil & Structural | Piling - Robotic Docking System | Piling - Robotic Docking System | Table | EA | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 | N |  | -
[9 empty] | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 | N
[9 empty] | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 | N
[9 empty] | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8 | N
[9 empty] | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N
A.1.4 |  | Civil |  | Piling + IDT Civil & Structural | Piling - LT Cable Hanger System | Piling - LT Cable Hanger System | Inverter | EA | Pre Pour Inspection - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 | N |  | -
[9 empty] | Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Alignment & Top level of Column Post by Auto Level & Piano wie and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 | N
[9 empty] | Pile Capping - Pre-Pour | Cleaning of top surface of pile, checking of Dia and Depth of Pile Cap Mould, Alignment & Top level of Pile Cap as per drawing and concrete pouring works, Concreting Works (Mixing points) if mixing thorugh Ajax Floori. | C_9_2 | N
[9 empty] | Post Pour Inspection | Alignment & Top level of Column Post by Auto Level & Piano wire, Pile capping height & level and Application of Protective coating on piles as per SOP | C_8 | N
[9 empty] | Routine Testing | Routine testing of piles (PIT, LLT if any), after 14 days of pile casting | No Checklist; only testing report to be uploaded | N
A.2.1 |  | Civil |  | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block | Not Applicable | Pre Pour Inspection for Micro Piling - Grid Marking & Coordinate Checking | Grid Marking & Cordinate Checking | C_9_1 | Y |  | -
[9 empty] | Pre Pour Inspection for Micro Piling - Checking of Boring Dimensions, Leveling and Concrete Pouring | Checking of Boring , Dia and Depth of Bore, Checking of pile cage, Top level of cage, cover, preparation of starter and concrete pouring works. Concreting Works (Mixing points), if mixing thorugh Ajax Floori (not required for RMC) | C_9_2 | Y
[9 empty] | Pre Pour Inspection for Column & Slab - Cast-in-Situ | Fixing of reinforcements (as per BBS), positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Cordinates & Location of opening, cut-outs (Size as per drawing) upto concreting works (mixing & pouring). | C_1 | N
[9 empty] | Post Pour Inspection for Column & Slab - Cast-in-Situ | Physical Dimension of structure as per drawing & appearnce (free of defect, deformations, etc.,.) and curing etc. | C_8 | N
[9 empty] | Canopy Erection with Sheeting after grouting | Fixing of nut & bolts in erected structure prior to final allignment check and tightening | C_11, C_12 | N
[9 empty] | Grouting | Readiness of grouting area (hacking, cleaning, soaking, shuttering,mixing,cube sampling works), grout pouring and acceptance of grout cube strength test results | C_34 | N
[9 empty] | Cable Support Strructure (above slab) |  |  | N | Require Checklist for this
[9 empty] | Cable Support Strructure (below slab) |  |  | N
A.2.2 |  | Civil |  | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block | Not Applicable | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16 | Y |  | -
[9 empty] | Gravel filling | Filling of suitable size gravels / sand as per drawing (Approved source material, physically Tested as per SFQP & accepted by Quality) | C_27 | N
[9 empty] | Sand Relative Density Test | To check the relative density of sand | C_15 | Y
[9 empty] | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying & finishing upto required level | C_36 | N
[9 empty] | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and upto concreting works | C_1 | N
[9 empty] | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8 | N
[9 empty] | Pre Pour Inspection for Ist Lift Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1 | N
[9 empty] | Post Pour Inspection for Ist Lift Wall | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8 | N
[9 empty] | Backfiling Layer Wise | Layer-wise filling, compaction & testing in each layer untill achieving accepted test result. | C_16 | N
[9 empty] | Pre Pour Inspection for 2nd Lift Wall with Rail | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing, Shuttering tightness, verticality, alignment checking prior to concreting and concreting works | C_1 | N
[9 empty] | Post Pour Inspection for 2nd Lift Wall Rail | Physical Dimension of structure & location of supported super-structures as per drawing,curing & appearnce (free of defect, deformations, etc.,.) and appllication of protecting coating paint | C_8 | N
A.2.3 |  | Civil |  | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block | Not Applicable | Sub Grade Compaction Test & Leveling | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16 | Y |  | -
[9 empty] | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level | C_36 | N
[9 empty] | Pre Pour Inspection for RCC Block | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and concreting works | C_1 | N
[9 empty] | Post Pour Inspection for RCC Block | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8 | N
A.2.4 |  | Civil |  | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block | Not Applicable | Sub Grade Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16 | Y |  | -
[9 empty] | Pre Pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36 | N
[9 empty] | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1 | N
[9 empty] | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8 | N
A.2.5 |  | Civil |  | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block | Not Applicable | Levelling & Compaction Test | Levelling & compaction test of base & Laying of soil/sub-grade material | C_16 | Y |  | -
[9 empty] | Rubble Soling Test | Laying of requisite size rubble soling material upto compaction | C_27 | N
[9 empty] | Pre-pour Inspection for PCC | Level & Grid Marking for PCC Laying up to required level and concreting works | C_36 | N
[9 empty] | Pre Pour Inspection for Raft | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment concreting works | C_1 | Y
[9 empty] | Post Pour Inspection for Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) with rectifications if any. And appllication of protecting coating paint | C_8 | Y
[9 empty] | Pre Pour Inspection for Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1 | Y
[9 empty] | Post Pour Inspection for Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8 | Y
[9 empty] | Pre Pour Inspection for Slab | Fixing & tighntness of shuttering supports, leak-proof arranegments, Reinforcement fixing, positioning of pockets/inserts/embedments. And upto concreting works | C_1 | Y
[9 empty] | Post Pour Inspection for Slab | Surface level/slope & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectification of defects if any | C_8 | Y
[9 empty] | Leak Test (If any), Rectification of defects (if any) & Acceptance of corrections action taken | Leak Test | C_8 | Y
A.2.6 |  | Civil |  | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block | Not Applicable | Sub Grade Compaction Test (including rubble soiling) | Levelling & compaction test of base & Laying of rubble | C_16 | N |  | -
[9 empty] | Pre Pour Inspection for Sump PCC | Level & Grid Marking for PCC Laying & finishing upto required level and concreting works | C_36 | N
[9 empty] | Pre Pour Inspection for Sump Raft | Fixing of reinforcements as per drawing prior to shutter board fixing, positioning of inserts & embedments (if any) and concreting works | C_1 | N
[9 empty] | Post Pour Inspection for Sump Raft | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.) | C_8 | N
[9 empty] | Pre Pour Inspection for Dyke Wall | Fixing of reinforcements, positioning of support structure, inserts & embedments (if any), as per drawing prior to shutter board fixing and Shuttering tightness, verticality, alignment, and upto concreting works | C_1 | N
[9 empty] | Post Pour Inspection for Dyke Wall | Physical Dimension of structure & location of supported super-structures as per drawing & appearnce (free of defect, deformations, etc.,.). Rectifications ofdefects if any. And appllication of protecting coating paint | C_8 | N
B.1.1 |  | Civil |  | MMS Installation | MMS Installation | MMS Installation | Table | EA | If Tracker: Tracker Alignment, Tightening & Torquing up to Torque Tube incl. Transmission Shaft If Fixed Tilt: Fixed Tilt Alignment, Tightening & Torquing up to bracing, perlin and all asembly parts | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | Tracker: C_29_1 Fixed Tilt: C_28_1 | N |  |  | A.1.1
C.1.1 |  | Civil |  | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | Module Installation | Module Installation | Table | EA | If Tracker: Tracker: Module Alignment, Tightening & Torquing incl. U bolt & purlin If Fixed Tilt: Fixed Tilt: Module Alignment, Tightening & Torquing incl. purline | If Tracker: - Final Inspection of assembly (for purlin, transimission asembly, Grounding cable, module, Antena, electrical wiring, binder & Communication box assembly) as per OEM manual - Rotation test of Tracker after the installation of module If Fixed Tilt: Final Inspection of assembly (for purlin, Grounding cable, module and assembly parts ) | Tracker: C_29_2 Fixed Tilt: C_28_2 | N |  |  |  | B.1.1
C.2.1 |  | Civil |  | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of binders/clips, bridges, docking & reverse stations | Table | EA | Final Inspection of alignment, torquing of docking station, Flexible bridge, return station | Inspection Checklist for Installation of Cleaning Robot Structures | OEM Specific Checklist (Airtouch, Leapting, Sol Bright) | N |  |  |  |  | C.1.1,A1.3,B1.1
C.3.1 |  | Civil |  | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block | Not Applicable | Fencing pole concrete | Markig of locations of posts, hole depth, Alignment, Verticality & level of Fence Post & concreting works as per drawing | C_47 | N |  |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.1
[9 empty] | Fixing of Fencing wire, concertina, Gates as per drawing with painting | Fixing of Fencing wire, concertina, Gates as per drawing with painting | C_10 | N
C.3.2 |  | Civil |  | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Gravel Laying | Block | Not Applicable | Gravel filling | Inspection of Gravel Filling Works | C_27 | N |  |  |  |  | C.3.1, D.1.6, D.2.1, D.2.3, D.3.1
D.1.1 |  | Electrical |  | AC / LT Network | AC/LT Network - Equipment Installation & Testing | Transformer | Block | Not Applicable | IDT and Accessories Installation | IDT Installation along with Accessories | A1 | N |  |  | A.2.2
[9 empty] | Oil Filtration | Oil Filtration process, IDT Testing | A2 | N
[9 empty] | IDT Testing | IDT Testing Report | No Checklist; only testing report to be uploaded | N
[9 empty] | HT, LT and Control Cable Termination, Equipment Earthing | LT and Control Cable Lugging, Crimping, Sleeving, HV side HT cable end termination, Torquing, Equipment body Earthing | A3 | N | How to segragate cable termination check to avoid repeatition
D.1.2 |  | Electrical |  | AC / LT Network | AC/LT Network - Equipment Installation & Testing | HT Panel | Block | Not Applicable | HT Panel Installation & Testing | Panel installation and Panel testing | C1 + Upload of Testing Report | N |  |  | A.2.1
[9 empty] | Cable Termination & Equipment Body Earthing | Cable Lugging, Crimping, Sleeving, HT cable end termination, Torquing, Equipment body Earthing | C2 | N | How to segragate cable termination check to avoid repeatition
D.1.3 |  | Electrical |  | AC / LT Network | AC/LT Network - Equipment Installation & Testing | LT Panel | Block | Not Applicable | LT Panel Installation & Testing | Panel installation and Panel testing | B1 + Upload of Testing Report | N |  |  | A.2.1
[9 empty] | Cable Termination & Equipment Body Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | B2 | N | How to segragate cable termination check to avoid repeatition
D.1.4 |  | Electrical |  | AC / LT Network | AC/LT Network - Equipment Installation & Testing | Auxiliary Transformer | Block | Not Applicable | Auxiliary Transformer Installation & Testing | Auxiliary transformer installation as per OEM Manual/Drawing and Testing | D1 | N |  |  | A.2.3
[9 empty] | Cable Termination & Equipment Body Earthing | Cable Lugging, Crimping, Sleeving, Torquing, Equipment body Earthing | D2 | N | How to segragate cable termination check to avoid repeatition
D.1.5 |  | Electrical |  | AC / LT Network | AC/LT Network - Equipment Installation & Testing | Others - NIFPS | Block | Not Applicable | NIFPS Installation & Testing | NIFPS Installation & Testing | No Checklist; only testing report to be uploaded | Y |  |  | A.2.4
D.1.6 |  | Electrical |  | AC / LT Network | AC/LT Network - Equipment Installation & Testing | Others - Lightning Arrester | Block | Not Applicable | LA installation & testing | LA installation & testing |  |  | Is there a checklist or testing report to be uploaded? | -
D.1.7 |  | Electrical |  | AC / LT Network | AC/LT Network - Equipment Installation & Testing | Others - Lighting & other fixtures | Block | Not Applicable | Fixture and wiring installation | Fixture and wiring installation - auxiliary power components |  |  | Is there a checklist or testing report to be uploaded? |  | A.2.1
D.2.1 |  | Electrical |  | AC / LT Network | AC/LT Network - Cable Laying & Cable Management System | LT Cable Laying - Inverter to IDT Station (up to LT Panel) | Inverter | KM | Cable drum IR test and Cable hanging for above-ground section | Cable drum IR test and Cable hanging for above-ground section | F2 | N |  |  |  | D.2.5
D.2.2 |  | Electrical |  | AC / LT Network | AC/LT Network - Cable Laying & Cable Management System | LT Cable Termination - Inverter to IDT Station (up to LT Panel) | Inverter | Not Applicable | Cable Termination & Equipment Body Earthing | Cable Lugging, Crimping, Sleeving, Torquing | F3 | N | How to segragate cable termination check to avoid repeatition |  |  |  | D.2.1, E.1.1, D.1.3
D.2.3 |  | Electrical |  | AC / LT Network | AC/LT Network - Cable Laying & Cable Management System | LT Cable Laying - Inside IDT Station (LT Power Cables + Control Cables) | Block | Not Applicable | LT Cable Laying Works for underground section | Trench excavation, sand bedding, HDPE & cable laying, PUFF sealing & final backfilling for underground section of LT cable | F2 | N |  |  | A.2.1, A.2.2, A.2.3, A.2.4
D.2.4 |  | Electrical |  | AC / LT Network | AC/LT Network - Cable Laying & Cable Management System | LT Cable Termination - Inside IDT Station | Block | Not Applicable | Cable Termination & Equipment Body Earthing | Cable Lugging, Crimping, Sleeving, Torquing | F3 | N | How to segragate cable termination check to avoid repeatition |  |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.3
D.2.5 |  | Electrical |  | AC / LT Network | AC/LT Network - Cable Laying & Cable Management System | LT Cable Mgmt System Laying | Block | Not Applicable | Messenger wire hanging | Messenger wire hanging | F1 | N |  |  | A.1.4
D.3.1 |  | Electrical |  | AC / LT Network | AC/LT Network - Earthing | Grid Earthing | Block | Not Applicable | Grid Earthing work & Testing | Grid Earthing work & Testing | D2 | N |  |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.1.6
E.1.1 |  | Electrical |  | DC Network | DC Network - Equipment Installation & Testing | String Inverter | Inverter | EA | Inverter Works | Inverter installation; LT Cable Lugging, Crimping, Sleeving & Torquing; Equipment body Earthing Ensure each individual string is formed with exactly 28 Nos of Solar PV Modules, having prominent and visible separation markings |  | N | Is there a checklist or testing report to be uploaded? |  | A.1.2
E.2.1 |  | Electrical |  | DC Network | DC Network - Cable Laying & Cable Management System | DC Cable Works | Inverter | KM | Trench excavation, DC cable laying, dressing, conduiting and PU foam sealing | Trench excavation, DC cable laying, dressing, conduiting (Modules to Inverter) | H1 | N |  |  |  |  | C.1.1
E.2.2 |  | Electrical |  | DC Network | DC Network - Cable Laying & Cable Management System | DC Cable Termination | Inverter | KM | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | MC4 connection, VOC Testing, Cable dressing, ferrule checking and PU foam sealing | H2 | N | [5 empty] | E.1.1, E.2.1
E.3.1 |  | Electrical |  | DC Network | DC Network - Earthing | Earthing of tables | Table | Not Applicable | Table Earthing work & Testing | Grid Earthing work & Testing | D2 | N |  |  |  | B.1.1
Note on F5: Hemdeep Padalia: Service Code will be mapped to a unique sub-package. This is will eventually be set in SAP
Note on L27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Which checklist to use - C_9 and C_14 are for MMS piling and not HT/LT platform? Reply: Corrected
Note on L36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on L75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory

## Inter-process linkage for RFIs (hidden)
Inter-Process Linkage Mapping (to be used for RFI staging)
To be discussed
| As defined in PULSE+DRS Platform Master Data | As per SAP PO Defined Item Text | As per SAP PO Defined Line Item Text | As defined in PULSE+DRS Platform Master Data | To be selected by Contractor during creation of RFI |  | As per the SAP PO UoM
# | Package | Sub-Package | Activity | Sub-Activity | Min. Unit of RFI (Per Table / Per Inverter / Per Block) | Variant for Qty Selection | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checklist Number | Inspection Checkpoints | Activity Dependency
[10 empty] | 1 | 2 | 3 | 4 | 5
A.1.1 | Civil | Piling + IDT Civil & Structural | Piling | Piling - for MMS | Table |  | EA |  | A.1.1 - Pre Pour Inspection - Grid Marking & Coordinate Checking | -
A.1.2 - Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring
A.1.3 - Post Pour Inspection
A.1.4 - Routine Testing (Report comes after 15 days)
A.1.2 | Civil | Piling + IDT Civil & Structural | Piling | Piling - for Inverter | Inverter |  | EA |  | A.1.1 - Pre Pour Inspection - Grid Marking & Coordinate Checking | -
A.1.2 - Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring
A.1.3 - Post Pour Inspection
A.1.4 - Routine Testing
A.1.3 | Civil | Piling + IDT Civil & Structural | Piling | Piling - for Robot | Table |  | EA |  | A.1.1 - Pre Pour Inspection - Grid Marking & Coordinate Checking | -
A.1.2 - Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring
A.1.3 - Post Pour Inspection
A.1.4 - Routine Testing
A.1.4 | Civil | Piling + IDT Civil & Structural | Piling | Piling - for LT Cable | Inverter |  | EA |  | A.1.1 - Pre Pour Inspection - Grid Marking & Coordinate Checking | -
A.1.2 - Pre Pour Inspection - Checking of Boring Dimensions, Leveling and Concrete Pouring
A.1.3 - Post Pour Inspection
A.1.4 - Routine Testing
A.2.1 | Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - HT / LT Platform | Block |  | Not Applicable |  | [Optional] A.2.1 - Pre Pour Inspection for Micro Piling - Grid Marking & Coordinate Checking | -
[Optional] A.2.2 - Pre Pour Inspection for Micro Piling - Checking of Boring Dimensions, Leveling and Concrete Pouring
A.2.3 - Pre Pour Inspection for Column & Slab - Cast-in-Situ
A.2.4 - Post Pour Inspection for Column & Slab - Cast-in-Situ
A.2.5 - Canopy Erection with Sheeting after grouting
A.2.6 - Grouting
A.2.2 | Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Transformer Platform | Block |  | Not Applicable |  | [Optional] A.3.1 - Sub Grade Compaction Test | -
A.3.2 - Gravel filling
[Optional] A.3.3 - Sand Relative Density Test
A.3.4 - Pre Pour Inspection for PCC
A.3.5 - Pre Pour Inspection for Raft
A.3.6 - Post Pour Inspection for Raft
A.3.7 - Pre Pour Inspection for Ist Lift Wall
A.3.8 - Post Pour Inspection for Ist Lift Wall
A.3.9 - Backfiling Layer Wise
A.3.10 - Pre Pour Inspection for 2nd Lift Wall with Rail
A.3.11 - Post Pour Inspection for 2nd Lift Wall Rail
A.2.3 | Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Aux Transformer Platform | Block |  | Not Applicable |  | [Optional] A.6.1 - Sub Grade Compaction Test & Leveling | -
A.6.2 - Pre Pour Inspection for PCC
A.6.3 - Pre Pour Inspection for RCC Block
A.6.4 - Post Pour Inspection for RCC Block
A.2.4 | Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - NIFPS Foundation | Block |  | Not Applicable |  | [Optional] A.7.1 - Sub Grade Compaction Test | -
A.7.2 - Pre Pour Inspection for PCC
A.7.3 - Pre Pour Inspection for Wall
A.7.4 - Post Pour Inspection for Wall
A.2.5 | Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - BOP | Block |  | Not Applicable |  | [Optional] A.5.1 - Levelling & Compaction Test | -
A.5.2 - Rubble Soling Test
A.5.3 - Pre-pour Inspection for PCC
A.5.4 - Pre Pour Inspection for Raft
A.5.5 - Post Pour Inspection for Raft
A.5.6 - Pre Pour Inspection for Wall
A.5.7 - Post Pour Inspection for Wall
A.5.8 - Pre Pour Inspection for Slab
A.5.9 - Post Pour Inspection for Slab
A.5.10 - Leak Test (If any), Rectification of defects (if any) & Acceptance of corrections action taken
A.2.6 | Civil | Piling + IDT Civil & Structural | IDT Civil & Structural | IDT Civil - Sump | Block |  | Not Applicable |  | A.4.1 - Sub Grade Compaction Test (including rubble soiling) | -
A.4.2 - Pre Pour Inspection for Sump PCC
A.4.3 - Pre Pour Inspection for Sump Raft
A.4.4 - Post Pour Inspection for Sump Raft
B.1.1 | Civil | MMS Installation | MMS Installation | MMS Installation | Table |  | EA |  | If Tracker: B.1.1 - Tracker Alignment, Tightening & Torquing up to Torque Tube incl. Transmission Shaft If Fixed Tilt: B.1.1 - Fixed Tilt Alignment, Tightening & Torquing up to bracing, perlin and all asembly parts |  | A.1.1
C.1.1 | Civil | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | Module Installation | Module Installation | Table |  | EA |  | If Tracker: C.1.1 - Tracker: Module Alignment, Tightening & Torquing incl. U bolt & purlin If Fixed Tilt: C.1.1 - Fixed Tilt: Module Alignment, Tightening & Torquing incl. purline |  |  | B.1.1
C.2.1 | Civil | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of binders/clips | Table |  | EA |  | C.2.1 - Final Inspection of alignment, torquing of docking station, Flexible bridge, return station |  |  |  | C.1.1
C.2.2 | Civil | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of bridges | Table |  | EA |  | C.2.1 - Final Inspection of alignment, torquing of docking station, Flexible bridge, return station |  |  |  | C.1.1
C.2.3 | Civil | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | Robot Structure Installation | Installation of docking & reverse stations | Table |  | EA |  | C.2.1 - Final Inspection of alignment, torquing of docking station, Flexible bridge, return station |  |  | A.1.3, B.1.1
C.3.1 | Civil | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Fencing | Block |  | Not Applicable |  | C.3.1 - Fencing pole concrete |  |  | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.1
C.3.2 - Fixing of Fencing wire, concertina, Gates as per drawing with painting
C.3.2 | Civil | Module Installation, Robot Structure Installation, IDT Fencing & Gravel Laying | IDT Fencing & Gravel Laying | IDT Gravel Laying | Block |  | Not Applicable |  | A.3.2 - Gravel filling |  |  |  | C.3.1, D.1.6, D.2.1, D.2.3, D.3.1
D.1.1 | Electrical | AC / LT Network | Equipment Installation & Testing | Transformer | Block | [5 empty] | A.2.2
D.1.2 |  | AC / LT Network | Equipment Installation & Testing | HT Panel | Block | [5 empty] | A.2.1
D.1.3 |  | AC / LT Network | Equipment Installation & Testing | LT Panels | Block | [5 empty] | A.2.1
D.1.4 |  | AC / LT Network | Equipment Installation & Testing | Auxiliary Transformer | Block | [5 empty] | A.2.3
D.1.5 |  | AC / LT Network | Equipment Installation & Testing | Others - NIFPS | Block | [5 empty] | A.2.4
D.1.6 |  | AC / LT Network | Equipment Installation & Testing | Others - Lightning Arrester | Block |  |  |  |  | -
D.1.7 |  | AC / LT Network | Equipment Installation & Testing | Others - Lighting & other fixtures | Block | [5 empty] | A.2.1
D.2.1 |  | AC / LT Network | LT Cable & Cable Mgmt System | LT Cable Laying - Inverter to IDT Station (up to LT Panel) | Inverter | [6 empty] | D.2.5
D.2.2 |  | AC / LT Network | LT Cable & Cable Mgmt System | LT Cable Termination - Inverter to IDT Station (up to LT Panel) | Inverter | [7 empty] | D.2.1, E.1.1, D.1.3
D.2.3 |  | AC / LT Network | LT Cable & Cable Mgmt System | LT Cable Laying - Inside IDT Station (LT Power Cables + Control Cables) | Block | [5 empty] | A.2.1, A.2.2, A.2.3, A.2.4
D.2.4 |  | AC / LT Network | LT Cable & Cable Mgmt System | LT Cable Termination - Inside IDT Station | Block | [7 empty] | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.2.3
D.2.5 |  | AC / LT Network | LT Cable & Cable Mgmt System | LT Cable Mgmt System Laying | Block | [5 empty] | A.1.4
D.3.1 |  | AC / LT Network | Earthing | Earthing | Block | [6 empty] | D.1.1, D.1.2, D.1.3, D.1.4, D.1.5, D.1.6
E.1.1 |  | DC Network | String Inverter Installation & Testing | String Inverter | Inverter | [5 empty] | A.1.2
E.2.1 |  | DC Network | DC Cable | DC Cable Laying | Inverter | [7 empty] | C.1.1
E.2.2 |  | DC Network | DC Cable | DC Cable Termination | Inverter | [8 empty] | E.1.1, E.2.1
E.3.1 |  | DC Network | Earthing | Earthing of tables | Table | [6 empty] | B.1.1
Note on K23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Which checklist to use - C_9 and C_14 are for MMS piling and not HT/LT platform?
Note on K30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory
Note on K57: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Club with Post-Pour inspection? Reply: No
Note on K58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rubble soiling is separate or clubbed? Also, is sub-grade compaction test compulsory for sump? Reply: Clubbed and both mandatory
Note on K69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Optional or mandatory? Reply: Mandatory