## Activity-Checklist_07.02.26
AGEL Wind Projects Activity Master with Inspection Checklists Mapping
Sr. No. | Package | Sub-Package | Activity | Sub-Activity | Unit of RFI (Per WTG) | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checkpoint Code | Inspection Checkpoint Name | Inspection Checkpoint Description | Inspection Checklist Name | Inspection Checklist Document | Is the Inspection Checkpoint Optional? | Preceding Inspection Checkpoint to be completed before raising RFI | Remarks
A1.1 | CIVIL | Stone Column | Stone Column Installation | Pre-Activity Work | Per WTG | EA | A1.1.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.1 | CIVIL | Stone Column | Stone Column Installation | Stone Column Work | Per WTG | EA | A1.1.2 | Inspection of Stone Column | Dia of vibro float, Depth calibration censer, Crane verticality angle, Free Energy e.g. Ams/Bar/Torque, TBM Inspection, Grid Marking & Cordinate Checking, Depth verification, Stone column installation graph inspection onsite. Aggregate Stock measurement to ensure minimum initial 10 columns. Aggregate consumption. | Stone Column Inspection Protocol for Vibro-Non Vibro Method | Stone Column Inspection Protocol for Vibro-Non Vibro Method | Y | A1.1.1
A1.1 | CIVIL | Stone Column | Stone Column Installation | Post-Activity Work | Per WTG | EA | A1.1.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.1.2
A1.2 | CIVIL | Stone Column | Plate Load Test | Pre-Activity Work | Per WTG | EA | A1.2.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.1.2
A1.2 | CIVIL | Stone Column | Plate Load Test | Plate Load Test | Per WTG | EA | A1.2.2 | Excavation and Sand Blanket for PLT | Depth verification from Cut off level, Inspect Actual and Drawing Co-ordinate of 3 Stone column, Sand Blanket 150 mm of 2 layer with achive minimum 95% Compaction test. | Excavation and Sand Blanketing Work for PLT | Excavation and Sand Blanketing work for PLT | Y | A1.2.1
A1.2 | CIVIL | Stone Column | Plate Load Test | Plate Load Test | Per WTG | EA | A1.2.3 | PLT Test Preparation/Inspection | Test bed prepration, Kentledge load setup, Inspection of all PLT Relevent Certificates | Plate Load Test Pre Inspection for WTG Stone Column | Plate Load Test Pre Inspection for WTG Stone Column | Y | A1.2.2
A1.2 | CIVIL | Stone Column | Plate Load Test | Plate Load Test | Per WTG | EA | A1.2.4 | Plate Load Test | Deflection / Settelement measurement at test load | Plate Load Test of WTG Stone Column | Plate Load Test of WTG Stone Column | Y | A1.2.3
A1.2 | CIVIL | Stone Column | Plate Load Test | Post-Activity Work | Per WTG | EA | A1.2.5 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.2.4
A1.3 | CIVIL | WTG Foundation | Excavation | Pre-Activity Work | Per WTG | EA | A1.3.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.2.4
A1.3 | CIVIL | WTG Foundation | Excavation | Excavation | Per WTG | EA | A1.3.2 | Preliminary Inspection | Excavated dia and depth/level, Soil strata | Excavation Checklist | Excavation checklist | Y | A1.3.1
A1.3 | CIVIL | WTG Foundation | Excavation | Post-Activity Work | Per WTG | EA | A1.3.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.3.2
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Pre-Activity Work | Per WTG | EA | A1.4.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.3.2
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 1 | Per WTG | EA | A1.4.2 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.1
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 2 | Per WTG | EA | A1.4.3 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.2
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 3 | Per WTG | EA | A1.4.4 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.3
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 4 | Per WTG | EA | A1.4.5 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.4
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 5 | Per WTG | EA | A1.4.6 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.5
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Post-Activity Work | Per WTG | EA | A1.4.7 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.4.6
A1.5 | CIVIL | WTG Foundation | Plum Concrete | Pre-Activity Work | Per WTG | EA | A1.5.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.4.6
A1.5 | CIVIL | WTG Foundation | Plum Concrete | Plum Concrete Layer 1 | Per WTG | EA | A1.5.2 | Routine Inspection | Material Inspection, Thickness and Compaction | Plum Concrete Checklist | Plum concrete | Y | A1.5.1
A1.5 | CIVIL | WTG Foundation | Plum Concrete | Plum Concrete Layer 2 | Per WTG | EA | A1.5.3 | Routine Inspection | Material Inspection, Thickness and Compaction | Plum Concrete Checklist | Plum concrete | Y | A1.5.2
A1.5 | CIVIL | WTG Foundation | Plum Concrete | Post-Activity Work | Per WTG | EA | A1.5.4 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.5.3
A1.6 | CIVIL | WTG Foundation | PCC | Pre-Activity Work | Per WTG | EA | A1.6.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.5.3
A1.6 | CIVIL | WTG Foundation | PCC | PCC | Per WTG | EA | A1.6.2 | PCC | Dimensions, Level, Concrete Grade, Quantity, As cast Finishing, Curing | PCC Checklist | PCC checklist | Y | A1.6.1
A1.6 | CIVIL | WTG Foundation | PCC | Post-Activity Work | Per WTG | EA | A1.6.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.6.2
A1.7 | CIVIL | WTG Foundation | Bottom Anchor Flange | Pre-Activity Work | Per WTG | EA | A1.7.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.6.2
A1.7 | CIVIL | WTG Foundation | Bottom Anchor Flange | Bottom Anchor Flange and Stud Erection | Per WTG | EA | A1.7.2 | Routine Inspection | Flange level, Bolt alignmenet, Torquing, serial number of flange and stud | Bottom Flange Level Checklist | Bottom Flange Level checklist | Y | A1.7.1
A1.7 | CIVIL | WTG Foundation | Bottom Anchor Flange | Post-Activity Work | Per WTG | EA | A1.7.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.7.2
A1.8 | CIVIL | WTG Foundation | Reinforcement Binding | Pre-Activity Work | Per WTG | EA | A1.8.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.7.2
A1.8 | CIVIL | WTG Foundation | Reinforcement Binding | Reinforcement Bottom Layer | Per WTG | EA | A1.8.2 | Routine Inspection | Cover Block, Dia, Nos of steel, Position and condition, Lapping, Binding | Reinforcement Checklist | Reinforcement checklist | Y | A1.8.1
A1.8 | CIVIL | WTG Foundation | Reinforcement Binding | Reinforcement Top Layer | Per WTG | EA | A1.8.3 | Routine Inspection | Cover Block, Dia, Nos of steel, Position and condition, Lapping, Binding | Reinforcement Checklist | Reinforcement checklist | Y | A1.8.2
A1.8 | CIVIL | WTG Foundation | Reinforcement Binding | Post-Activity Work | Per WTG | EA | A1.8.4 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.8.3
A1.9 | CIVIL | WTG Foundation | WTG Foundation | Pre-Activity Work | Per WTG | EA | A1.9.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.8.3
A1.9 | CIVIL | WTG Foundation | WTG Foundation | WTG Foundation | Per WTG | EA | A1.9.2 | Pre Pour Inspection - WTG Foundation | Final Reinforcement inspection, Shuttering, Earthing strip, DWC Conduit, Grout bucket along with top glange fixing, Raw material testing, Cleaning, Vibrator, Boom Placer, Nitobond, Curing compound, Manpower, Mason, Cement | Pre-Pour Checklist | Pre pour checklist | Y | A1.9.1
A1.9 | CIVIL | WTG Foundation | WTG Foundation | WTG Foundation | Per WTG | EA | A1.9.3 | Post Pour Inspection - WTG Foundation | As cast finishing; Padestal, Stud & Flange level, Curing compound application | Post-Pour Checklist | Post pour checklist | Y | A1.9.2
A1.9 | CIVIL | WTG Foundation | WTG Foundation | Bitumen Painting of WTG Foundation | Per WTG | EA | A1.9.4 | Routine Inspection | Uniform painting and DFT checking | Bitumen Coating Painting Checklist | Bitumen coating Painting_inspection | Y | A1.9.3
A1.9 | CIVIL | WTG Foundation | WTG Foundation | Post-Activity Work | Per WTG | EA | A1.9.5 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.9.4
A1.10 | CIVIL | WTG Foundation | Top Flange Grouting | Pre-Activity Work | Per WTG | EA | A1.10.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.9.4
A1.10 | CIVIL | WTG Foundation | Top Flange Grouting | Top Flange Grouting | Per WTG | EA | A1.10.2 | Grouting | Flange level, Nitobond application, Water test, Grouting material tracibility, Cube casting, Curing | WTG Top Flange Grouting Checklist | Top Flange Grouting - WTG | Y | A1.10.1
A1.10 | CIVIL | WTG Foundation | Top Flange Grouting | Post-Activity Work | Per WTG | EA | A1.10.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.10.2
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Pre-Activity Work | Per WTG | EA | A1.11.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.10.2
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.2 | Backfiling Layer 1 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.1
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.3 | Backfiling Layer 2 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.2
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.4 | Backfiling Layer 3 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.3
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.5 | Backfiling Layer 4 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.4
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.6 | Backfiling Layer 5 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.5
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.7 | Backfiling Layer 6 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.6
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.8 | Backfiling Layer 7 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.7
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.9 | Backfiling Layer 8 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.8
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Post-Activity Work | Per WTG | EA | A1.11.10 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.11.9
A1.12 | CIVIL | WTG Foundation | Earthing Mesh | Pre-Activity Work | Per WTG | EA | A1.12.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.11.9
A1.12 | CIVIL | WTG Foundation | Earthing Mesh | Earthing Mesh | Per WTG | EA | A1.12.2 | Routine Inspection | Approved, Material, Mesh size as per drawing, Joints Welding and Protective paint. | Earthing Mesh Checklist | Earthing Mesh Checklist | Y | A1.12.1
A1.12 | CIVIL | WTG Foundation | Earthing Mesh | Post-Activity Work | Per WTG | EA | A1.12.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.12.2
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | Pre-Activity Work | Per WTG | EA | A1.13.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.12.2
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | Backfilling After Mesh Placement | Per WTG | EA | A1.13.2 | Backfiling Layer 9 | Level and Compaction | Backfilling Checklist | Backfiiling Checklist | Y | A1.13.1
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | Backfilling After Mesh Placement | Per WTG | EA | A1.13.3 | Backfiling Layer 10 | Level and Compaction | Backfilling Checklist | Backfiiling Checklist | Y | A1.13.2
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | GSB Layer | Per WTG | EA | A1.13.4 | GSB Layer | Material, Dimensions, Thickness, Slope, Compaction | GSB Inspection Checklist | GSB inspection checklist | Y | A1.13.3
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | Post-Activity Work | Per WTG | EA | A1.13.5 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.13.4
A1.14 | CIVIL | USS Civil and Structural | DT | Pre-Activity Work | Per WTG | EA | A1.14.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.14 | CIVIL | USS Civil and Structural | DT | Excavation | Per WTG | EA | A1.14.2 | Pre-Inspection | Dimensions, Level, Concrete Grade, Quantity, As cast Finishing, Curing | Excavation Checklist - General Works | Excavation checklist general works | Y | A1.14.1
A1.14 | CIVIL | USS Civil and Structural | DT | Backfilling | Per WTG | EA | A1.14.3 | Routine Inspection | Level and Compaction | Backfiiling Checklist | Backfiiling Checklist | Y | A1.14.2
A1.14 | CIVIL | USS Civil and Structural | DT | Gravel Laying below DT | Per WTG | EA | A1.14.4 | Routine Inspection | Level and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.14.3
A1.14 | CIVIL | USS Civil and Structural | DT | PCC | Per WTG | EA | A1.14.5 | Routine Inspection | Level,Concrete grade,Quantity and Finishing | PCC Checklist | PCC checklist | Y | A1.14.4
A1.14 | CIVIL | USS Civil and Structural | DT | Erection | Per WTG | EA | A1.14.6 | Routine Inspection | Pre/Post Erection & Grouting | Precast Elements Erection, Positioning & Grouting Checklist | Precast Elements Erection, Positioning & Grouting | Y | A1.14.5
A1.14 | CIVIL | USS Civil and Structural | DT | Bitumen Painting | Per WTG | EA | A1.14.7 | Routine Inspection | Surface finishing,uniformity, DFT check | Bitumen Coating Painting Checklist | Bitumen coating Painting_inspection | Y | A1.14.6
A1.14 | CIVIL | USS Civil and Structural | DT | Gravel Laying above FGL/Inside DT FDG | Per WTG | EA | A1.14.8 | Final Inspection | level,compaction. | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.14.7
A1.14 | CIVIL | USS Civil and Structural | DT | Post-Activity Work | Per WTG | EA | A1.14.9 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.14.8
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Pre-Activity Work | Per WTG | EA | A1.15.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Excavation | Per WTG | EA | A1.15.2 | Pre-Inspection | Level and Compaction | Excavation Checklist - General Works | Excavation checklist general works | Y | A1.15.1
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | PCC | Per WTG | EA | A1.15.3 | Routine Inspection | Dimensions, Level, Concrete Grade, Quantity, As cast Finishing. | PCC Checklist | PCC checklist | Y | A1.15.2
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Erection | Per WTG | EA | A1.15.4 | Routine Inspection | Pre/Post Erection & Grouting | Precast Elements Erection, Positioning & Grouting Checklist | Precast Elements Erection, Positioning & Grouting | Y | A1.15.3
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Bitumen Painting | Per WTG | EA | A1.15.5 | Routine Inspection | Surface finishing,uniformity, DFT check | Bitumen Coating Painting Checklist | Bitumen coating Painting_inspection | Y | A1.15.4
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Backfilling | Per WTG | EA | A1.15.6 | Routine Inspection | Level and Compaction | Backfiiling Checklist | Backfiiling Checklist | Y | A1.15.5
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Stair Case Erection | Per WTG | EA | A1.15.7 | Routine Inspection | level and Alingment | Precast Elements Erection, Positioning & Grouting Checklist | Precast Elements Erection, Positioning & Grouting | Y | A1.15.6
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Handrail Installation | Per WTG | EA | A1.15.8 | Final Inspection | Alingnment and Dimension, welding joint, | Checklist for Preacst Elements | Checklist for Preacst element | Y | A1.15.7
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Post-Activity Work | Per WTG | EA | A1.15.9 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.15.8
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Pre-Activity Work | Per WTG | EA | A1.16.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Excavation | Per WTG | EA | A1.16.2 | Pre-Inspection | Excavated dia and depth | Excavation Checklist - General Works | Excavation checklist general works | Y | A1.16.1
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | PCC | Per WTG | EA | A1.16.3 | Routine Inspection | level and Alingment | PCC Checklist | PCC checklist | Y | A1.16.2
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Erection | Per WTG | EA | A1.16.4 | Routine Inspection |  | Precast Elements Erection, Positioning & Grouting Checklist | Precast Elements Erection, Positioning & Grouting | Y | A1.16.3
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Backfilling | Per WTG | EA | A1.16.5 | Routine Inspection | Material,Level and Compaction | Backfiiling Checklist | Backfiiling Checklist | Y | A1.16.4
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Drain Pipe Connectivity | Per WTG | EA | A1.16.6 | Final Inspection | Level, Pipe connectivity | BOT Level and Pipe Connectivity Checklist | BOT level and pipe connectivity | Y | A1.16.5
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Post-Activity Work | Per WTG | EA | A1.16.7 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.16.6
A1.17 | CIVIL | USS Civil and Structural | Fencing | Pre-Activity Work | Per WTG | EA | A1.17.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.16.6, A1.15.8, A1.14.8
A1.17 | CIVIL | USS Civil and Structural | Fencing | Backfilling | Per WTG | EA | A1.17.2 | Pre-Inspection | Level and Compaction | Backfiiling Checklist | Backfiiling Checklist | Y | A1.17.1
A1.17 | CIVIL | USS Civil and Structural | Fencing | Fencing Post Casting | Per WTG | EA | A1.17.3 | Routine Inspection | Dimension,Alingnment | Fencing Post Checklist | Fencing Post checklist | Y | A1.17.2
A1.17 | CIVIL | USS Civil and Structural | Fencing | Barbed Wire Installation | Per WTG | EA | A1.17.4 | Routine Inspection | Material, Alingnment, j -hookes | Barbed Wire checklist | barbed checklist | Y | A1.17.3
A1.17 | CIVIL | USS Civil and Structural | Fencing | White Wash | Per WTG | EA | A1.17.5 | Routine Inspection | White wash of post | White Wash Checklist | White wash checklist | Y | A1.17.4
A1.17 | CIVIL | USS Civil and Structural | Fencing | Gate Installation | Per WTG | EA | A1.17.6 | Routine Inspection | Dimension, Alingnment | Fencing Gate Installation Checklist | Fencing Gate installation | Y | A1.17.5
A1.17 | CIVIL | USS Civil and Structural | Fencing | Gravel Laying | Per WTG | EA | A1.17.7 | Final Inspection | Level and Compaction | Gravel Laying Checklist | Gravel Laying Checklist | Y | A1.17.6
A1.17 | CIVIL | USS Civil and Structural | Fencing | Post-Activity Work | Per WTG | EA | A1.17.8 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.17.7
A1.18 | CIVIL | Crane Pad | Crane Pad | Pre-Activity Work | Per WTG | EA | A1.18.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.18 | CIVIL | Crane Pad | Crane Pad | OGL | Per WTG | EA | A1.18.2 | Pre-Inspection | Dimension,Level and Compaction | OGL Checklist | OGL checklist | Y | A1.18.1
A1.18 | CIVIL | Crane Pad | Crane Pad | Boulder Laying | Per WTG | EA | A1.18.3 | Routine Inspection | Dimension, Level and thickness | Boulder Laying Checklist | Boulder laying checklist | Y | A1.18.2
A1.18 | CIVIL | Crane Pad | Crane Pad | GSB Laying | Per WTG | EA | A1.18.4 | Final Inspection | Dimension,Thickness and Compaction. | GSB Laying Checklist | GSB laying checklist | Y | A1.18.3
A1.18 | CIVIL | Crane Pad | Crane Pad | Post-Activity Work | Per WTG | EA | A1.18.5 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.18.4
B1.1 | ELECTRICAL | USS Electrical | Oil Filled Transformer | Pre-Activity Work | Per WTG | EA | B1.1.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.14.8 | Remove
B1.1 | ELECTRICAL | USS Electrical | Oil Filled Transformer | Transformer and Accessories Installation | Per WTG | EA | B1.1.2 | Transformer and Accessories Installation Inspection | 1.Transformer Installation along with Accessories installation, 2.LT/HT Cable Termination. 3. Equipment body Earthing. 4. Control Cable Work. 5. Neutral Earthing. 6. IDT Support Installation(Fins Vibration Strip, Radiator Support, HV/LV Support.) | IDT Oil Filled Transformer Field Quality Protocol | Adani/QA/PRT/E/029 (Erection Section) | Y | B1.1.1
B1.1 | ELECTRICAL | USS Electrical | Oil Filled Transformer | Post-Activity Work | Per WTG | EA | B1.1.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.1.2
B1.2 | ELECTRICAL | USS Electrical | HT Switchboard | Pre-Activity Work | Per WTG | EA | B1.2.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.15.8 | Remove
B1.2 | ELECTRICAL | USS Electrical | HT Switchboard | HT Panel and Accessories Installation | Per WTG | EA | B1.2.2 | HT Panel and Accessories Installation Inspection | 1.HT Panel Installation along with accessories. 2. Earthing. 3.Control Cable termination. 4 HT Cable Termination. 5. LPBS. | HT Switchboard Field Quality Protocol | Adani/QA/PRT/E/017 (Erection Setion) | Y | B1.2.1
B1.2 | ELECTRICAL | USS Electrical | HT Switchboard | Post-Activity Work | Per WTG | EA | B1.2.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.2.2
B1.3 | ELECTRICAL | USS Electrical | Earthing | Pre-Activity Work | Per WTG | EA | B1.3.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
B1.3 | ELECTRICAL | USS Electrical | Earthing | Earthing Flat Work | Per WTG | EA | B1.3.2 | Earthing Flat Work Inspection | 1. Earthing Flat Laying/ Mesh Work. 2. Welding Work. 3. Pit Installation. | Earthing Field Quality Protocol | Adani/QA/PRT/E/013 (Erection Section) | Y | B1.3.1
B1.3 | ELECTRICAL | USS Electrical | Earthing | Post-Activity Work | Per WTG | EA | B1.3.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.3.2
B1.4 | ELECTRICAL | USS Electrical | Cable Tray | Pre-Activity Work | Per WTG | EA | B1.4.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
B1.4 | ELECTRICAL | USS Electrical | Cable Tray | LT Cable Tray Work | Per WTG | EA | B1.4.2 | LT Cable Tray Work Inspection | 1. Marking and Level of Cable Tray. 2. Auggring Work for Cable Tray. 3. Tray Installation. 4. Tray Support Clamp Installation. 5. Cable Laying on Tray with Clamp tightness. 6. Tray Cover Installation. 7. Touch-up Paint work of LT Tray Support leg Copping. | Cable Tray Field Quality Protocol | Adani/QA/PRT/E/006 (Erection Section) | Y | B1.4.1
B1.4 | ELECTRICAL | USS Electrical | Cable Tray | Post-Activity Work | Per WTG | EA | B1.4.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.4.2
B1.5 | ELECTRICAL | USS Electrical | Illumination | Pre-Activity Work | Per WTG | EA | B1.5.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
B1.5 | ELECTRICAL | USS Electrical | Illumination | Light Pole Work | Per WTG | EA | B1.5.2 | Light Pole Work Inspection | 1. Auggring for Light Pole Foundation. 2. Casting of Light Pole. 3.Control cable Termination of Light pole. | Illumination Field Quality Protocol | Adani/QA/PRT/E/018 (Erection Setion) | Y | B1.5.1
B1.5 | ELECTRICAL | USS Electrical | Illumination | Post-Activity Work | Per WTG | EA | B1.5.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.5.2
B1.6 | ELECTRICAL | USS Electrical | LT Switchboard | Pre-Activity Work | Per WTG | EA | B1.6.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
B1.6 | ELECTRICAL | USS Electrical | LT Switchboard | ACDB Work | Per WTG | EA | B1.6.2 | ACDB Work Inspection | 1. ACBD Installation work. 2. Control Cable Termination Work. 3. ACDB Earthing Work. 4. LPBS Installation Work. | LT Switchboards Field Quality Protocol | Adani/QA/PRT/E/023 (Erection Section) | Y | B1.6.1
B1.6 | ELECTRICAL | USS Electrical | LT Switchboard | Post-Activity Work | Per WTG | EA | B1.6.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.6.2
B1.7 | ELECTRICAL | USS Electrical | LT Cabling | Pre-Activity Work | Per WTG | EA | B1.7.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.4.2
B1.7 | ELECTRICAL | USS Electrical | LT Cabling | LT Cable Laying | Per WTG | EA | B1.7.2 | LT Cable Laying Inspection | 1. LT Cable Laying work. 2. Cable Termination Work. 2. Lugging + Gland Fixing work. | LT Cabling Field Quality Protocol | Adani/QA/PRT/E/022A (Laying Section) | Y | B1.7.1
B1.7 | ELECTRICAL | USS Electrical | LT Cabling | Post-Activity Work | Per WTG | EA | B1.7.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.7.2
B1.8 | ELECTRICAL | UG Cable | HT Cabling | Pre-Activity Work | Per WTG | EA | B1.8.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.2.2
B1.8 | ELECTRICAL | UG Cable | HT Cabling | HT Cable Laying | Per WTG | EA | B1.8.2 | HT Cable Laying Inspection | 3. HT Cable- Laying. i. Cable laying with proper routin. ii. Briks laying properly. iii. Second layer sand beding. iv. Backfilling of trench also with FO cable and Caution Tap. | HT Cable Field Quality Protocol | Adani/QA/PRT/E/016 (Laying Section) | Y | B1.8.1
B1.8 | ELECTRICAL | UG Cable | HT Cabling | Post-Activity Work | Per WTG | EA | B1.8.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.8.2
C1.1 | MECHANICAL | WTG Erection | Tower Erection | Pre-Activity Work | Per WTG | EA | C 1.1.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.13.4 | Remove
C1.1 | MECHANICAL | WTG Erection | Tower Erection | Tower Erection | Per WTG | EA | C 1.1.2 | Tower Erection Inspection | Tower section from bottom to top including foundation and bottom platform | Tower Erection Checklist | Prepratation of Foundation.docx, Installation of bottom platform onto the foundation.docx, Installation of lower tower segment (5th tower section.docx, Installation of lower tower segment (4th tower section).docx, Installation of lower tower segment (3rd tower section).docx, Installation of lower tower segment (2nd tower section).docx, Installation of lower tower segment (1st tower section).docx | Y | C 1.1.1
C1.1 | MECHANICAL | WTG Erection | Tower Erection | Post-Activity Work | Per WTG | EA | C 1.1.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C 1.1.2
C1.2 | MECHANICAL | WTG Erection | Nacelle | Pre-Activity Work | Per WTG | EA | C1.2.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C 1.1.2
C1.2 | MECHANICAL | WTG Erection | Nacelle | Nacelle Installation | Per WTG | EA | C1.2.2 | Nacelle Installation Inspection | Nacelle Mounting and Installation | Nacelle Installation Checklist | Mounting Nacelle.docx | Y | C1.2.1
C1.2 | MECHANICAL | WTG Erection | Nacelle | Post-Activity Work | Per WTG | EA | C1.2.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.2.2
C1.3 | MECHANICAL | WTG Erection | Hub, DT and Blades | Pre-Activity Work | Per WTG | EA | C1.3.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.2.2
C1.3 | MECHANICAL | WTG Erection | Hub, DT and Blades | Hub, DT and Blades Installation | Per WTG | EA | C1.3.2 | Hub, DT and Blades Installation Inspection | Rotor Hub, Drive Train and Blades Mounting and Installation | Rotor Hub, Drive Train and Blades Installation Checklist | Mounting Drive train.docx, Mounting Turn Drive.docx, Preparation of Nacelle Roof TOP and Mounting.docx, Mounting The Rotor Hub.docx, Mounting the blade lifting traverse.docx, Mounting the 1st rotor blade.docx, Mounting the 2nd rotor blade.docx, Mounting the 3rd rotor blade.docx | Y | C1.3.1
C1.3 | MECHANICAL | WTG Erection | Hub, DT and Blades | Post-Activity Work | Per WTG | EA | C1.3.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.3.2
C1.4 | MECHANICAL | WTG Erection | Generator | Pre-Activity Work | Per WTG | EA | C1.4.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.3.2
C1.4 | MECHANICAL | WTG Erection | Generator | Generator Installation | Per WTG | EA | C1.4.2 | Generator Installation Inspection | Generator Alignment and Installation | Generator Installatio Checklist | Mounting the generator coupling.docx | Y | C1.4.1
C1.4 | MECHANICAL | WTG Erection | Generator | Post-Activity Work | Per WTG | EA | C1.4.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.4.2
C1.5 | MECHANICAL | WTG Erection | Nacelle Top Cover | Pre-Activity Work | Per WTG | EA | C1.5.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.4.2
C1.5 | MECHANICAL | WTG Erection | Nacelle Top Cover | Nacelle Top Cover Installation | Per WTG | EA | C1.5.2 | Nacelle Top Cover Installation Inspection | Nacelle Top Cover Installation | Nacelle Top Cover Installation Checklist | Mounting the nacelle roof (covers).docx | Y | C1.5.1
C1.5 | MECHANICAL | WTG Erection | Nacelle Top Cover | Post-Activity Work | Per WTG | EA | C1.5.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.5.2
C1.6 | MECHANICAL | WTG Erection | Torquing | Pre-Activity Work | Per WTG | EA | C1.6.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.5.2
C1.6 | MECHANICAL | WTG Erection | Torquing | Torquing | Per WTG | EA | C1.6.2 | Torquing Inspection | Torquing Inspection | Torquing Checklist | No Checklist Q: Duly-Filled Torquing Sheet Submitted to Concerned AGEL Team for Review? | Y | C1.6.1
C1.6 | MECHANICAL | WTG Erection | Torquing | Post-Activity Work | Per WTG | EA | C1.6.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.6.2
C1.7 | MECHANICAL | WTG Erection | MCC Audit | Pre-Activity Work | Per WTG | EA | C1.7.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.6.2
C1.7 | MECHANICAL | WTG Erection | MCC Audit | MCC Audit | Per WTG | EA | C1.7.2 | MCC Audit | MCC Audit | MCC Audit Report | No Checklist Q: Duly-Filled MCC Audit Report Submitted to Concerned AGEL Team for Review? | Y | C1.7.1
C1.7 | MECHANICAL | WTG Erection | MCC Audit | Post-Activity Work | Per WTG | EA | C1.7.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.7.2
C1.8 | MECHANICAL | WTG Erection | Re-Verification Audit | Pre-Activity Work | Per WTG | EA | C1.8.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.7.2
C1.8 | MECHANICAL | WTG Erection | Re-Verification Audit | Re-Verification Audit | Per WTG | EA | C1.8.2 | Re-Verification Audit | Re-Verification Audit | Re-Verification Audit Report | No Checklist Q: Duly-Filled Re-Verification Audit Report Submitted to Concerned AGEL Team for Review? | Y | C1.8.1
C1.8 | MECHANICAL | WTG Erection | Re-Verification Audit | Post-Activity Work | Per WTG | EA | C1.8.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.8.2
Note on E4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on H4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to validate by EoD Reply: Validated
Note on N4: Hemdeep Padalia: For cases of "Y", a checkbox is required on Inspection Checkpoint screen like "Inspection check not required" (select button)
Note on O4: Hemdeep Padalia: This will be used to sequence inspection checkpoints (within a sub-activity) and order of sub-activity in which RFI can be created

## Activity-Checklist_23.04.26
AGEL Wind Projects Activity Master with Inspection Checklists Mapping
Sr. No. | Package | Sub-Package | Activity | Sub-Activity | Unit of RFI (Per WTG) | Unit of Measure for Optional Qty. Input by Contractor | Inspection Checkpoint Code | Inspection Checkpoint Name | Inspection Checkpoint Description | Inspection Checklist Name | Inspection Checklist Document | Is the Inspection Checkpoint Optional? | Preceding Inspection Checkpoint to be completed before raising RFI | Remarks
A1.1 | CIVIL | Stone Column | Stone Column Installation | Pre-Activity Work | Per WTG | EA | A1.1.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.1 | CIVIL | Stone Column | Stone Column Installation | Stone Column Work | Per WTG | EA | A1.1.2 | Inspection of Stone Column | Dia of vibro float, Depth calibration sensor, Crane verticality angle, Free Energy e.g. Ams/Bar/Torque, TBM Inspection, Grid Marking & Cordinate Checking, Depth verification, Stone column installation graph inspection onsite. Aggregate Stock measurement to ensure minimum initial 10 columns. Aggregate consumption. | Stone Column Inspection Protocol for Vibro-Non Vibro Method | Stone Column Inspection Protocol for Vibro-Non Vibro Method | Y | A1.1.1
A1.1 | CIVIL | Stone Column | Stone Column Installation | Post-Activity Work | Per WTG | EA | A1.1.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.1.2
A1.2 | CIVIL | Stone Column | Plate Load Test | Pre-Activity Work | Per WTG | EA | A1.2.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.1.2
A1.2 | CIVIL | Stone Column | Plate Load Test | Plate Load Test | Per WTG | EA | A1.2.2 | Excavation and Sand Blanket for PLT | Depth verification from Cut off level, Inspect Actual and Drawing Co-ordinate of 3 Stone column, Sand Blanket 150 mm of 2 layer with achive minimum 95% Compaction test. | Excavation and Sand Blanketing Work for PLT | Excavation and Sand Blanketing work for PLT | Y | A1.2.1
A1.2 | CIVIL | Stone Column | Plate Load Test | Plate Load Test | Per WTG | EA | A1.2.3 | PLT Test Preparation/Inspection | Test bed prepration, Kentledge load setup, Inspection of all PLT Relevent Certificates | Plate Load Test Pre Inspection for WTG Stone Column | Plate Load Test Pre Inspection for WTG Stone Column | Y | A1.2.2
A1.2 | CIVIL | Stone Column | Plate Load Test | Plate Load Test | Per WTG | EA | A1.2.4 | Plate Load Test | Deflection / Settelement measurement at test load | Plate Load Test of WTG Stone Column | Plate Load Test of WTG Stone Column | Y | A1.2.3
A1.2 | CIVIL | Stone Column | Plate Load Test | Post-Activity Work | Per WTG | EA | A1.2.5 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.2.4
A1.3 | CIVIL | WTG Foundation | Excavation | Pre-Activity Work | Per WTG | EA | A1.3.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.2.4
A1.3 | CIVIL | WTG Foundation | Excavation | Excavation | Per WTG | EA | A1.3.2 | Preliminary Inspection | Excavated dia and depth/level, Soil strata | Excavation Checklist | Excavation checklist | Y | A1.3.1
A1.3 | CIVIL | WTG Foundation | Excavation | Post-Activity Work | Per WTG | EA | A1.3.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.3.2
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Pre-Activity Work | Per WTG | EA | A1.4.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.3.2
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 1 | Per WTG | EA | A1.4.2 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.1
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 2 | Per WTG | EA | A1.4.3 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.2
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 3 | Per WTG | EA | A1.4.4 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.3
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 4 | Per WTG | EA | A1.4.5 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.4
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Blanket/GSB Layer 5 | Per WTG | EA | A1.4.6 | Routine Inspection | Material Inspection, Thickness and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.4.5
A1.4 | CIVIL | WTG Foundation | Blanket Layer/GSB Layer | Post-Activity Work | Per WTG | EA | A1.4.7 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.4.6
A1.5 | CIVIL | WTG Foundation | Plum Concrete | Pre-Activity Work | Per WTG | EA | A1.5.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.4.6
A1.5 | CIVIL | WTG Foundation | Plum Concrete | Plum Concrete Layer 1 | Per WTG | EA | A1.5.2 | Routine Inspection | Material Inspection, Thickness and Compaction | Plum Concrete Checklist | Plum concrete | Y | A1.5.1
A1.5 | CIVIL | WTG Foundation | Plum Concrete | Plum Concrete Layer 2 | Per WTG | EA | A1.5.3 | Routine Inspection | Material Inspection, Thickness and Compaction | Plum Concrete Checklist | Plum concrete | Y | A1.5.2
A1.5 | CIVIL | WTG Foundation | Plum Concrete | Post-Activity Work | Per WTG | EA | A1.5.4 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.5.3
A1.6 | CIVIL | WTG Foundation | PCC | Pre-Activity Work | Per WTG | EA | A1.6.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.5.3
A1.6 | CIVIL | WTG Foundation | PCC | PCC | Per WTG | EA | A1.6.2 | PCC | Dimensions, Level, Concrete Grade, Quantity, As cast Finishing, Curing | PCC Checklist | PCC checklist | Y | A1.6.1
A1.6 | CIVIL | WTG Foundation | PCC | Post-Activity Work | Per WTG | EA | A1.6.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.6.2
A1.7 | CIVIL | WTG Foundation | Bottom Anchor Flange | Pre-Activity Work | Per WTG | EA | A1.7.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.6.2
A1.7 | CIVIL | WTG Foundation | Bottom Anchor Flange | Bottom Anchor Flange and Stud Erection | Per WTG | EA | A1.7.2 | Routine Inspection | Flange level, Bolt alignmenet, Torquing, serial number of flange and stud | Bottom Flange Level Checklist | Bottom Flange Level checklist | Y | A1.7.1
A1.7 | CIVIL | WTG Foundation | Bottom Anchor Flange | Post-Activity Work | Per WTG | EA | A1.7.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.7.2
A1.8 | CIVIL | WTG Foundation | Reinforcement Binding | Pre-Activity Work | Per WTG | EA | A1.8.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.7.2
A1.8 | CIVIL | WTG Foundation | Reinforcement Binding | Reinforcement Bottom Layer | Per WTG | EA | A1.8.2 | Routine Inspection | Cover Block, Dia, Nos of steel, Position and condition, Lapping, Binding | Reinforcement Checklist | Reinforcement checklist | Y | A1.8.1
A1.8 | CIVIL | WTG Foundation | Reinforcement Binding | Reinforcement Top Layer | Per WTG | EA | A1.8.3 | Routine Inspection | Cover Block, Dia, Nos of steel, Position and condition, Lapping, Binding | Reinforcement Checklist | Reinforcement checklist | Y | A1.8.2
A1.8 | CIVIL | WTG Foundation | Reinforcement Binding | Post-Activity Work | Per WTG | EA | A1.8.4 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.8.3
A1.9a | CIVIL | WTG Foundation | WTG Foundation | Pre-Activity Work | Per WTG | EA | A1.9a.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.8.3
A1.9a | CIVIL | WTG Foundation | WTG Foundation | WTG Foundation | Per WTG | EA | A1.9a.2 | Pre Pour Inspection - WTG Foundation | Final Reinforcement inspection, Shuttering, Earthing strip, DWC Conduit, Grout bucket along with top glange fixing, Raw material testing, Cleaning, Vibrator, Boom Placer, Nitobond, Curing compound, Manpower, Mason, Cement | Pre-Pour Checklist | Pre pour checklist | Y | A1.9a.1
A1.9a | CIVIL | WTG Foundation | WTG Foundation | WTG Foundation | Per WTG | EA | A1.9a.3 | Post Pour Inspection - WTG Foundation | As cast finishing; Padestal, Stud & Flange level, Curing compound application | Post-Pour Checklist | Post pour checklist | Y | A1.9a.2
A1.9a | CIVIL | WTG Foundation | WTG Foundation | Post-Activity Work | Per WTG | EA | A1.9a.4 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.9a.3
A1.9b | CIVIL | WTG Foundation | WTG Foundation - Bitumen Painting | Pre-Activity Work | Per WTG | EA | A1.9b.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.9a.4
A1.9b | CIVIL | WTG Foundation | WTG Foundation - Bitumen Painting | Bitumen Painting of WTG Foundation | Per WTG | EA | A1.9b.2 | Routine Inspection | Uniform painting and DFT checking | Bitumen Coating Painting Checklist | Bitumen coating Painting_inspection | Y | A1.9b.1
A1.9b | CIVIL | WTG Foundation | WTG Foundation - Bitumen Painting | Post-Activity Work | Per WTG | EA | A1.9b.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.9b.2
A1.10 | CIVIL | WTG Foundation | Top Flange Grouting | Pre-Activity Work | Per WTG | EA | A1.10.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.9.4
A1.10 | CIVIL | WTG Foundation | Top Flange Grouting | Top Flange Grouting | Per WTG | EA | A1.10.2 | Grouting | Flange level, Nitobond application, Water test, Grouting material tracibility, Cube casting, Curing | WTG Top Flange Grouting Checklist | Top Flange Grouting - WTG | Y | A1.10.1
A1.10 | CIVIL | WTG Foundation | Top Flange Grouting | Post-Activity Work | Per WTG | EA | A1.10.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.10.2
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Pre-Activity Work | Per WTG | EA | A1.11.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.10.2
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.2 | Backfiling Layer 1 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.1
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.3 | Backfiling Layer 2 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.2
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.4 | Backfiling Layer 3 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.3
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.5 | Backfiling Layer 4 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.4
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.6 | Backfiling Layer 5 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.5
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.7 | Backfiling Layer 6 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.6
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.8 | Backfiling Layer 7 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.7
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Backfilling Before Mesh Placement | Per WTG | EA | A1.11.9 | Backfiling Layer 8 | Level and Compaction | Backfilling Checklist | Backfilling Checklist | Y | A1.11.8
A1.11 | CIVIL | WTG Foundation | Backfilling (Before Mesh) | Post-Activity Work | Per WTG | EA | A1.11.10 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.11.9
A1.12 | CIVIL | WTG Foundation | Earthing Mesh | Pre-Activity Work | Per WTG | EA | A1.12.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.11.9
A1.12 | CIVIL | WTG Foundation | Earthing Mesh | Earthing Mesh | Per WTG | EA | A1.12.2 | Routine Inspection | Approved, Material, Mesh size as per drawing, Joints Welding and Protective paint. | Earthing Mesh Checklist | Earthing Mesh Checklist | Y | A1.12.1
A1.12 | CIVIL | WTG Foundation | Earthing Mesh | Post-Activity Work | Per WTG | EA | A1.12.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.12.2
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | Pre-Activity Work | Per WTG | EA | A1.13.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.12.2
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | Backfilling After Mesh Placement | Per WTG | EA | A1.13.2 | Backfiling Layer 9 | Level and Compaction | Backfilling Checklist | Backfiiling Checklist | Y | A1.13.1
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | Backfilling After Mesh Placement | Per WTG | EA | A1.13.3 | Backfiling Layer 10 | Level and Compaction | Backfilling Checklist | Backfiiling Checklist | Y | A1.13.2
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | GSB Layer | Per WTG | EA | A1.13.4 | GSB Layer | Material, Dimensions, Thickness, Slope, Compaction | GSB Inspection Checklist | GSB inspection checklist | Y | A1.13.3
A1.13 | CIVIL | WTG Foundation | Backfilling (After Mesh) | Post-Activity Work | Per WTG | EA | A1.13.5 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.13.4
A1.14 | CIVIL | USS Civil and Structural | DT | Pre-Activity Work | Per WTG | EA | A1.14.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.14 | CIVIL | USS Civil and Structural | DT | Excavation | Per WTG | EA | A1.14.2 | Pre-Inspection | Dimensions, Level, Concrete Grade, Quantity, As cast Finishing, Curing | Excavation Checklist - General Works | Excavation checklist general works | Y | A1.14.1
A1.14 | CIVIL | USS Civil and Structural | DT | Backfilling | Per WTG | EA | A1.14.3 | Routine Inspection | Level and Compaction | Backfiiling Checklist | Backfiiling Checklist | Y | A1.14.2
A1.14 | CIVIL | USS Civil and Structural | DT | Gravel Laying below DT | Per WTG | EA | A1.14.4 | Routine Inspection | Level and Compaction | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.14.3
A1.14 | CIVIL | USS Civil and Structural | DT | PCC | Per WTG | EA | A1.14.5 | Routine Inspection | Level,Concrete grade,Quantity and Finishing | PCC Checklist | PCC checklist | Y | A1.14.4
A1.14 | CIVIL | USS Civil and Structural | DT | Erection | Per WTG | EA | A1.14.6 | Routine Inspection | Pre/Post Erection & Grouting | Precast Elements Erection, Positioning & Grouting Checklist | Precast Elements Erection, Positioning & Grouting | Y | A1.14.5
A1.14 | CIVIL | USS Civil and Structural | DT | Bitumen Painting | Per WTG | EA | A1.14.7 | Routine Inspection | Surface finishing,uniformity, DFT check | Bitumen Coating Painting Checklist | Bitumen coating Painting_inspection | Y | A1.14.6
A1.14 | CIVIL | USS Civil and Structural | DT | Gravel Laying above FGL/Inside DT FDG | Per WTG | EA | A1.14.8 | Final Inspection | level,compaction. | Stone Blanket Layer Checklist | Stone Blanket Layer checklist | Y | A1.14.7
A1.14 | CIVIL | USS Civil and Structural | DT | Post-Activity Work | Per WTG | EA | A1.14.9 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.14.8
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Pre-Activity Work | Per WTG | EA | A1.15.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Excavation | Per WTG | EA | A1.15.2 | Pre-Inspection | Level and Compaction | Excavation Checklist - General Works | Excavation checklist general works | Y | A1.15.1
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | PCC | Per WTG | EA | A1.15.3 | Routine Inspection | Dimensions, Level, Concrete Grade, Quantity, As cast Finishing. | PCC Checklist | PCC checklist | Y | A1.15.2
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Erection | Per WTG | EA | A1.15.4 | Routine Inspection | Pre/Post Erection & Grouting | Precast Elements Erection, Positioning & Grouting Checklist | Precast Elements Erection, Positioning & Grouting | Y | A1.15.3
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Bitumen Painting | Per WTG | EA | A1.15.5 | Routine Inspection | Surface finishing,uniformity, DFT check | Bitumen Coating Painting Checklist | Bitumen coating Painting_inspection | Y | A1.15.4
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Backfilling | Per WTG | EA | A1.15.6 | Routine Inspection | Level and Compaction | Backfiiling Checklist | Backfiiling Checklist | Y | A1.15.5
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Stair Case Erection | Per WTG | EA | A1.15.7 | Routine Inspection | level and Alingment | Precast Elements Erection, Positioning & Grouting Checklist | Precast Elements Erection, Positioning & Grouting | Y | A1.15.6
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Handrail Installation | Per WTG | EA | A1.15.8 | Final Inspection | Alingnment and Dimension, welding joint, | Checklist for Preacst Elements | Checklist for Preacst element | Y | A1.15.7
A1.15 | CIVIL | USS Civil and Structural | HT Foundation | Post-Activity Work | Per WTG | EA | A1.15.9 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.15.8
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Pre-Activity Work | Per WTG | EA | A1.16.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Excavation | Per WTG | EA | A1.16.2 | Pre-Inspection | Excavated dia and depth | Excavation Checklist - General Works | Excavation checklist general works | Y | A1.16.1
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | PCC | Per WTG | EA | A1.16.3 | Routine Inspection | level and Alingment | PCC Checklist | PCC checklist | Y | A1.16.2
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Erection | Per WTG | EA | A1.16.4 | Routine Inspection |  | Precast Elements Erection, Positioning & Grouting Checklist | Precast Elements Erection, Positioning & Grouting | Y | A1.16.3
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Backfilling | Per WTG | EA | A1.16.5 | Routine Inspection | Material,Level and Compaction | Backfiiling Checklist | Backfiiling Checklist | Y | A1.16.4
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Drain Pipe Connectivity | Per WTG | EA | A1.16.6 | Final Inspection | Level, Pipe connectivity | BOT Level and Pipe Connectivity Checklist | BOT level and pipe connectivity | Y | A1.16.5
A1.16 | CIVIL | USS Civil and Structural | Burnt Oil Tank | Post-Activity Work | Per WTG | EA | A1.16.7 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.16.6
A1.17 | CIVIL | USS Civil and Structural | Fencing | Pre-Activity Work | Per WTG | EA | A1.17.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.16.6, A1.15.8, A1.14.8
A1.17 | CIVIL | USS Civil and Structural | Fencing | Backfilling | Per WTG | EA | A1.17.2 | Pre-Inspection | Level and Compaction | Backfiiling Checklist | Backfiiling Checklist | Y | A1.17.1
A1.17 | CIVIL | USS Civil and Structural | Fencing | Fencing Post Casting | Per WTG | EA | A1.17.3 | Routine Inspection | Dimension,Alingnment | Fencing Post Checklist | Fencing Post checklist | Y | A1.17.2
A1.17 | CIVIL | USS Civil and Structural | Fencing | Barbed Wire Installation | Per WTG | EA | A1.17.4 | Routine Inspection | Material, Alingnment, j -hookes | Barbed Wire checklist | barbed checklist | Y | A1.17.3
A1.17 | CIVIL | USS Civil and Structural | Fencing | White Wash | Per WTG | EA | A1.17.5 | Routine Inspection | White wash of post | White Wash Checklist | White wash checklist | Y | A1.17.4
A1.17 | CIVIL | USS Civil and Structural | Fencing | Gate Installation | Per WTG | EA | A1.17.6 | Routine Inspection | Dimension, Alingnment | Fencing Gate Installation Checklist | Fencing Gate installation | Y | A1.17.5
A1.17 | CIVIL | USS Civil and Structural | Fencing | Gravel Laying | Per WTG | EA | A1.17.7 | Final Inspection | Level and Compaction | Gravel Laying Checklist | Gravel Laying Checklist | Y | A1.17.6
A1.17 | CIVIL | USS Civil and Structural | Fencing | Post-Activity Work | Per WTG | EA | A1.17.8 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.17.7
A1.18 | CIVIL | Crane Pad | Crane Pad | Pre-Activity Work | Per WTG | EA | A1.18.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
A1.18 | CIVIL | Crane Pad | Crane Pad | OGL | Per WTG | EA | A1.18.2 | Pre-Inspection | Dimension,Level and Compaction | OGL Checklist | OGL checklist | Y | A1.18.1
A1.18 | CIVIL | Crane Pad | Crane Pad | Boulder Laying | Per WTG | EA | A1.18.3 | Routine Inspection | Dimension, Level and thickness | Boulder Laying Checklist | Boulder laying checklist | Y | A1.18.2
A1.18 | CIVIL | Crane Pad | Crane Pad | GSB Laying | Per WTG | EA | A1.18.4 | Final Inspection | Dimension,Thickness and Compaction. | GSB Laying Checklist | GSB laying checklist | Y | A1.18.3
A1.18 | CIVIL | Crane Pad | Crane Pad | Post-Activity Work | Per WTG | EA | A1.18.5 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.18.4
B1.1 | ELECTRICAL | USS Electrical | Oil Filled Transformer | Pre-Activity Work | Per WTG | EA | B1.1.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.14.6
B1.1 | ELECTRICAL | USS Electrical | Oil Filled Transformer | Transformer and Accessories Installation | Per WTG | EA | B1.1.2 | Transformer and Accessories Installation Inspection | 1.Transformer Installation along with Accessories installation, 2.LT/HT Cable Termination. 3. Equipment body Earthing. 4. Control Cable Work. 5. Neutral Earthing. 6. IDT Support Installation(Fins Vibration Strip, Radiator Support, HV/LV Support.) | IDT Oil Filled Transformer Field Quality Protocol | Adani/QA/PRT/E/029 (Erection Section) | Y | B1.1.1
B1.1 | ELECTRICAL | USS Electrical | Oil Filled Transformer | Post-Activity Work | Per WTG | EA | B1.1.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.1.2
B1.2 | ELECTRICAL | USS Electrical | HT Switchboard | Pre-Activity Work | Per WTG | EA | B1.2.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.15.4
B1.2 | ELECTRICAL | USS Electrical | HT Switchboard | HT Panel and Accessories Installation | Per WTG | EA | B1.2.2 | HT Panel and Accessories Installation Inspection | 1.HT Panel Installation along with accessories. 2. Earthing. 3.Control Cable termination. 4 HT Cable Termination. 5. LPBS. | HT Switchboard Field Quality Protocol | Adani/QA/PRT/E/017 (Erection Setion) | Y | B1.2.1
B1.2 | ELECTRICAL | USS Electrical | HT Switchboard | Post-Activity Work | Per WTG | EA | B1.2.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.2.2
B1.3 | ELECTRICAL | USS Electrical | Earthing | Pre-Activity Work | Per WTG | EA | B1.3.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
B1.3 | ELECTRICAL | USS Electrical | Earthing | Earthing Flat Work | Per WTG | EA | B1.3.2 | Earthing Flat Work Inspection | 1. Earthing Flat Laying/ Mesh Work. 2. Welding Work. 3. Pit Installation. | Earthing Field Quality Protocol | Adani/QA/PRT/E/013 (Erection Section) | Y | B1.3.1
B1.3 | ELECTRICAL | USS Electrical | Earthing | Post-Activity Work | Per WTG | EA | B1.3.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.3.2
B1.4 | ELECTRICAL | USS Electrical | Cable Tray | Pre-Activity Work | Per WTG | EA | B1.4.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
B1.4 | ELECTRICAL | USS Electrical | Cable Tray | LT Cable Tray Work | Per WTG | EA | B1.4.2 | LT Cable Tray Work Inspection | 1. Marking and Level of Cable Tray. 2. Auggring Work for Cable Tray. 3. Tray Installation. 4. Tray Support Clamp Installation. 5. Cable Laying on Tray with Clamp tightness. 6. Tray Cover Installation. 7. Touch-up Paint work of LT Tray Support leg Copping. | Cable Tray Field Quality Protocol | Adani/QA/PRT/E/006 (Erection Section) | Y | B1.4.1
B1.4 | ELECTRICAL | USS Electrical | Cable Tray | Post-Activity Work | Per WTG | EA | B1.4.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.4.2
B1.5 | ELECTRICAL | USS Electrical | Illumination | Pre-Activity Work | Per WTG | EA | B1.5.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
B1.5 | ELECTRICAL | USS Electrical | Illumination | Light Pole Work | Per WTG | EA | B1.5.2 | Light Pole Work Inspection | 1. Auggring for Light Pole Foundation. 2. Casting of Light Pole. 3.Control cable Termination of Light pole. | Illumination Field Quality Protocol | Adani/QA/PRT/E/018 (Erection Setion) | Y | B1.5.1
B1.5 | ELECTRICAL | USS Electrical | Illumination | Post-Activity Work | Per WTG | EA | B1.5.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.5.2
B1.6 | ELECTRICAL | USS Electrical | LT Switchboard | Pre-Activity Work | Per WTG | EA | B1.6.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | -
B1.6 | ELECTRICAL | USS Electrical | LT Switchboard | ACDB Work | Per WTG | EA | B1.6.2 | ACDB Work Inspection | 1. ACBD Installation work. 2. Control Cable Termination Work. 3. ACDB Earthing Work. 4. LPBS Installation Work. | LT Switchboards Field Quality Protocol | Adani/QA/PRT/E/023 (Erection Section) | Y | B1.6.1
B1.6 | ELECTRICAL | USS Electrical | LT Switchboard | Post-Activity Work | Per WTG | EA | B1.6.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.6.2
B1.7 | ELECTRICAL | USS Electrical | LT Cabling | Pre-Activity Work | Per WTG | EA | B1.7.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.4.2
B1.7 | ELECTRICAL | USS Electrical | LT Cabling | LT Cable Laying | Per WTG | EA | B1.7.2 | LT Cable Laying Inspection | 1. LT Cable Laying work. 2. Cable Termination Work. 2. Lugging + Gland Fixing work. | LT Cabling Field Quality Protocol | Adani/QA/PRT/E/022A (Laying Section) | Y | B1.7.1
B1.7 | ELECTRICAL | USS Electrical | LT Cabling | Post-Activity Work | Per WTG | EA | B1.7.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.7.2
B1.8 | ELECTRICAL | UG Cable | HT Cabling | Pre-Activity Work | Per WTG | EA | B1.8.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.2.2
B1.8 | ELECTRICAL | UG Cable | HT Cabling | HT Cable Laying | Per WTG | EA | B1.8.2 | HT Cable Laying Inspection | 3. HT Cable- Laying. i. Cable laying with proper routin. ii. Briks laying properly. iii. Second layer sand beding. iv. Backfilling of trench also with FO cable and Caution Tap. | HT Cable Field Quality Protocol | Adani/QA/PRT/E/016 (Laying Section) | Y | B1.8.1
B1.8 | ELECTRICAL | UG Cable | HT Cabling | Post-Activity Work | Per WTG | EA | B1.8.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | B1.8.2
C1.1 | MECHANICAL | WTG Erection | Tower Erection | Pre-Activity Work | Per WTG | EA | C 1.1.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | A1.13.4
C1.1 | MECHANICAL | WTG Erection | Tower Erection | Tower Erection | Per WTG | EA | C 1.1.2 | Tower Erection Inspection | Tower section from bottom to top including foundation and bottom platform | Tower Erection Checklist | Prepratation of Foundation.docx, Installation of bottom platform onto the foundation.docx, Installation of lower tower segment (5th tower section.docx, Installation of lower tower segment (4th tower section).docx, Installation of lower tower segment (3rd tower section).docx, Installation of lower tower segment (2nd tower section).docx, Installation of lower tower segment (1st tower section).docx | Y | C 1.1.1
C1.1 | MECHANICAL | WTG Erection | Tower Erection | Post-Activity Work | Per WTG | EA | C 1.1.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C 1.1.2
C1.2 | MECHANICAL | WTG Erection | Nacelle | Pre-Activity Work | Per WTG | EA | C1.2.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C 1.1.2
C1.2 | MECHANICAL | WTG Erection | Nacelle | Nacelle Installation | Per WTG | EA | C1.2.2 | Nacelle Installation Inspection | Nacelle Mounting and Installation | Nacelle Installation Checklist | Mounting Nacelle.docx | Y | C1.2.1
C1.2 | MECHANICAL | WTG Erection | Nacelle | Post-Activity Work | Per WTG | EA | C1.2.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.2.2
C1.3 | MECHANICAL | WTG Erection | Hub, DT and Blades | Pre-Activity Work | Per WTG | EA | C1.3.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.2.2
C1.3 | MECHANICAL | WTG Erection | Hub, DT and Blades | Hub, DT and Blades Installation | Per WTG | EA | C1.3.2 | Hub, DT and Blades Installation Inspection | Rotor Hub, Drive Train and Blades Mounting and Installation | Rotor Hub, Drive Train and Blades Installation Checklist | Mounting Drive train.docx, Mounting Turn Drive.docx, Preparation of Nacelle Roof TOP and Mounting.docx, Mounting The Rotor Hub.docx, Mounting the blade lifting traverse.docx, Mounting the 1st rotor blade.docx, Mounting the 2nd rotor blade.docx, Mounting the 3rd rotor blade.docx | Y | C1.3.1
C1.3 | MECHANICAL | WTG Erection | Hub, DT and Blades | Post-Activity Work | Per WTG | EA | C1.3.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.3.2
C1.4 | MECHANICAL | WTG Erection | Generator | Pre-Activity Work | Per WTG | EA | C1.4.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.3.2
C1.4 | MECHANICAL | WTG Erection | Generator | Generator Installation | Per WTG | EA | C1.4.2 | Generator Installation Inspection | Generator Alignment and Installation | Generator Installatio Checklist | Mounting the generator coupling.docx | Y | C1.4.1
C1.4 | MECHANICAL | WTG Erection | Generator | Post-Activity Work | Per WTG | EA | C1.4.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.4.2
C1.5 | MECHANICAL | WTG Erection | Nacelle Top Cover | Pre-Activity Work | Per WTG | EA | C1.5.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.4.2
C1.5 | MECHANICAL | WTG Erection | Nacelle Top Cover | Nacelle Top Cover Installation | Per WTG | EA | C1.5.2 | Nacelle Top Cover Installation Inspection | Nacelle Top Cover Installation | Nacelle Top Cover Installation Checklist | Mounting the nacelle roof (covers).docx | Y | C1.5.1
C1.5 | MECHANICAL | WTG Erection | Nacelle Top Cover | Post-Activity Work | Per WTG | EA | C1.5.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.5.2
C1.6 | MECHANICAL | WTG Erection | Torquing | Pre-Activity Work | Per WTG | EA | C1.6.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.5.2
C1.6 | MECHANICAL | WTG Erection | Torquing | Torquing | Per WTG | EA | C1.6.2 | Torquing Inspection | Torquing Inspection | Torquing Checklist | No Checklist Q: Duly-Filled Torquing Sheet Submitted to Concerned AGEL Team for Review? | Y | C1.6.1
C1.6 | MECHANICAL | WTG Erection | Torquing | Post-Activity Work | Per WTG | EA | C1.6.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.6.2
C1.7 | MECHANICAL | WTG Erection | MCC Audit | Pre-Activity Work | Per WTG | EA | C1.7.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.6.2
C1.7 | MECHANICAL | WTG Erection | MCC Audit | MCC Audit | Per WTG | EA | C1.7.2 | MCC Audit | MCC Audit | MCC Audit Report | No Checklist Q: Duly-Filled MCC Audit Report Submitted to Concerned AGEL Team for Review? | Y | C1.7.1
C1.7 | MECHANICAL | WTG Erection | MCC Audit | Post-Activity Work | Per WTG | EA | C1.7.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.7.2
C1.8 | MECHANICAL | WTG Erection | Re-Verification Audit | Pre-Activity Work | Per WTG | EA | C1.8.1 | Pre-Activity Checkpoint | Pre-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.7.2
C1.8 | MECHANICAL | WTG Erection | Re-Verification Audit | Re-Verification Audit | Per WTG | EA | C1.8.2 | Re-Verification Audit | Re-Verification Audit | Re-Verification Audit Report | No Checklist Q: Duly-Filled Re-Verification Audit Report Submitted to Concerned AGEL Team for Review? | Y | C1.8.1
C1.8 | MECHANICAL | WTG Erection | Re-Verification Audit | Post-Activity Work | Per WTG | EA | C1.8.3 | Post-Activity Checkpoint | Post-Activity Inspection Checks, Documents and Reports | - | - | Y | C1.8.2
Note on E4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Generate WMC at this level Reply: + allocate SOs at this level Reply: Yes, this is noted for SO-Activity-Block Mapping sheet
Note on H4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Hemdeep to validate by EoD Reply: Validated
Note on N4: Hemdeep Padalia: For cases of "Y", a checkbox is required on Inspection Checkpoint screen like "Inspection check not required" (select button)
Note on O4: Hemdeep Padalia: This will be used to sequence inspection checkpoints (within a sub-activity) and order of sub-activity in which RFI can be created

## Sheet1
Excavation | Tower Erection
Blanket Layer/GSB Layer | Nacelle
Plum Concrete | Hub, DT and Blades
PCC | Generator
Bottom Anchor Flange | Nacelle Top Cover
Reinforcement Binding | Torquing
WTG Foundation | MCC Audit
Top Flange Grouting | Re-Verification Audit
Backfilling (Before Mesh)
Earthing Mesh
Backfilling (After Mesh)